{"text_format":"1","workbook":"xlsx","n_sheets":6,"sheets":["Version","Calcul du rendement","T° retour condensation","Fichier météo UCCLE","Fichier météo StHubert","Données"],"not_rendered":{"charts":7,"images":1,"macros":1,"external_links":0,"defined_names":3,"comments":4,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Version","index":0,"n_rows":8,"n_cols":2,"rows_kept":8,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[]
[null,"Modifications juin 2023 - ICEDD"]
[null,"- Restriction des unités permises pour l'encodage des consommations de gaz: kWh PCS uniqumement (et non plus m³ en raison du caractère hétérogène et progressif de la conversion au gaz riche).\n- Ajout d'une explication complémentaire pour l'encodage des chaudières (ligne 105)."]

{"sheet":"Calcul du rendement","index":1,"n_rows":429,"n_cols":18,"rows_kept":429,"cut":false,"hidden":false,"merged":[[5,1,5,5],[9,1,9,6],[208,2,208,3],[16,8,16,9],[17,8,17,9],[18,8,18,9],[19,8,19,9],[195,2,195,3]]}
[]
[]
[null,"Evaluation du rendement saisonnier d'une ou d'un ensemble de chaudières"]
[]
[null,"Version 2023 - ICEDD"]
[null,"Ce programme permet d'estimer le rendement saisonnier d'une installation de production de chaleur existante."]
[]
[]
[]
[null,"Il est possible de tester des améliorations apportées à l'installaion. Par exemple, en remplaçant la ou les chaudières, en stoppant l'irrigation des chaudières à l'arrêt, en améliorant le réglage des brûleurs pour obtenir un meilleur rendement de combustion, en plaçant des brûleurs 2 allures, …"]
[]
[null,"- encodez les données relatives à votre situation dans les cases bleues."]
[null,"- les résultats sont repris dans les cases jaunes."]
[]
[null,"Données climatiques"]
[]
[null,"Zone pour données météo",null,null,null,null,"UCCLE",null,"Ordre de grandeur"]
[null,null,null,null,null,null,null,null,"- 8°C pour la région bruxelloise et le tournaisis"]
[null,null,null,null,null,null,null,null,"- 9°C pour la région namuroise et du centre"]
[null,"On considère que l'installation aurait dû être dimensionnée pour une température extérieure de :",null,null,null,null,-8,"°C","- 10°C pour le sud et nord-est"]
[]
[null,"Consommation de combustible"]
[]
[null,"Combustible utilisé par la chaufferie :"]
[]
[null,"Consommation annuelle de référence :",null,null,null,55000]
[]
[null,"Consommation annuelle de référence :",null,null,null,{"$f":"IF(Données!B11=3,'Calcul du rendement'!F26*Données!L5,'Calcul du rendement'!F26*Données!J5)","v":49610},"kWh PCI / an"]
[]
[null,"Caractéristiques d'occupation du bâtiment"]
[]
[null,"Horaire journalier de fonctionnement de l'installation :"]
[]
[null,null,"Choisissez les plages de fonctionnement de l'installation en régime \"jour\" (2 plages possibles) :"]
[]
[null,null,null,"Période 1 :","de",8,"h      à",18,"h"]
[null,null,null,"Période 2 :","de",null,"h      à",null,"h"]
[]
[null,"Horaire hebdomadaire :"]
[]
[]
[null,"Température de consigne de jour :",null,null,null,19,"°C"]
[null,"Température de consigne d'inoccupation :",null,null,null,16,"°C","Home/Hôpital","Bureaux","Habitat","Ecole "]
[null,"Estimation des apports solaires/apports internes :",null,null,null,2,"°C","3 °C","4 °C","3 °C","3 °C"]
[]
[]
[null,"Durée d'utilisation des chaudières :"]
[]
[null,null,null,null,"Jour","Mois"]
[null,null,"Arrêt du chauffage :",null,15,5]
[null,null,"Relance du chauffage :",null,15,9]
[]
[null,null,"Exemple : une installation arrêtée le 15 mai et relancée le 15 septembre"]
[]
[null,null,null,null,"Jour","Mois"]
[null,null,"Arrêt du chauffage :",null,15,5]
[null,null,"Relance du chauffage :",null,15,9]
[]
[null,"Durée totale d'utilisation :",null,null,{"$f":"IF(G17=\"StHubert\",'Fichier météo StHubert'!F20,'Fichier météo UCCLE'!F20)","v":5808},"heures/an"]
[]
[]
[null,"Description de l'installation"]
[]
[null,"Nombre de chaudières :",null,null,1,"(maximum 4)",null,{"$f":"IF(E64>4,\"Trop de chaudières !\",\"\")","v":""}]
[]
[null,"Régulation des chaudières :"]
[]
[]
[null,null,"Définition du mode de régulation via l'expérience de l'auditeur :"]
[]
[null,null,null,"1. Régulation des chaudières :"]
[]
[null,null,null,"2. Régulation des allures de brûleur :"]
[]
[null,null,null,null,"- dans le cas d'une installation de plus d'une chaudière avec simultanément des brûleurs 1 allure et 2 allures, on considérera que tous les brûleurs sont à 1 allure"]
[null,null,null,null,"- dans le cas d'une installation avec brûleurs modulants, ceux-ci devront être assimilés à des brûleurs 2 allures"]
[]
[]
[]
[null,null,"Régime de température des chaudières (température moyenne des chaudières durant la saison de chauffe) :",null,null,null,null,null,null,null,null,null,null,null,"Mode de régulation pris en considération :"]
[null,null,null,null,null,"Sur consigne aquastat en permanence (à 75°C)",null,null,null,null,null,null,null,null,"Régulation chaudières",3]
[null,null,null,null,null,"Température glissante avec limite basse (à 60°C)",null,null,null,null,null,null,null,null,"Régulation brûleurs",1]
[null,null,null,null,null,"Température glissante sans limite basse"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Choix cadre 21 :",1]
[null,null,null,null,"Température moyenne (départ - retour) estimée :",null,null,null,{"$f":"IF(P84=1,70,IF(P84=2,56,42))","v":70},"°C"]
[null,null,null,null,"Facteur de correction du coefficient de perte à l'arrêt :",null,null,null,{"$f":"((I85-20)/(70-20))^1.3","v":1}]
[]
[]
[]
[null,"Caractéristiques des chaudières (encodées dans l'ordre d'enclenchement d'une cascade éventuelle) :"]
[]
[null,null,null,"- les chaudières à condensation seront assimilées à des chaudières gaz brûleur pulsé à 2 allures"]
[]
[null,null,null,null,null,null,{"$f":"IF($E$64<1,\"-\",\"Chaudière 1\")","v":"Chaudière 1"},{"$f":"IF($E$64<2,\"-\",\"Chaudière 2\")","v":"-"},{"$f":"IF($E$64<3,\"-\",\"Chaudière 3\")","v":"-"},{"$f":"IF($E$64<4,\"-\",\"Chaudière 4\")","v":"-"}]
[null,null,null,null,"Type de chaudière :",null,null,null,null,null,null,null,null,null,1,1,1,1]
[]
[null,null,null,null,"Année de fabrication de la chaudière :",null,1980,1980]
[null,null,null,null,"Isolation de la chaudière :",null,null,null,null,null,null,null,null,null,1,2,1,2]
[]
[]
[null,null,null,null,null,null,null,"Pertes balayage :",null,1,"%"]
[null,null,null,null,null,null,null,"Mauvaise isolation :",null,0.75,"%"]
[null,null,null,null,null,null,null,"Facteur perte ambiance si mauvaise isolation :",null,1]
[]
[null,null,"Si brûleur fuel pulsé :",null,"Puissance nominale :",null,null,null,null,null,"kW",null,null,null,false,false,false,false]
[null,null,null,null,"Pression d'alimentation allure 1 :",null,null,null,null,null,"bars",null,null,null,false,false,false,false]
[null,null,null,null,"Calibre gicleur allure 1 :",null,null,null,null,null,"gal/h"]
[null,null,null,null,"Débit de fuel allure 1 :",null,{"$f":"IF(OR(Données!B5<>3,O95<>1),\"-\",ROUND(3.78*G107*(G106/6.89)^0.5,1))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5<>3,P95<>1),\"-\",ROUND(3.78*H107*(H106/6.89)^0.5,1))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5<>3,Q95<>1),\"-\",ROUND(3.78*I107*(I106/6.89)^0.5,1))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5<>3,R95<>1),\"-\",ROUND(3.78*J107*(J106/6.89)^0.5,1))","v":"-"},"litres/h"]
[null,null,null,null,"Puissance réelle allure 1 :",null,{"$f":"IF(OR(Données!B5<>3,O95<>1),\"-\",G108*Données!J5)","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5<>3,P95<>1),\"-\",H108*Données!J5)","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5<>3,Q95<>1),\"-\",I108*Données!J5)","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5<>3,R95<>1),\"-\",J108*Données!J5)","v":"-"},"kW"]
[null,null,null,null,"Pression d'alimentation allure 2 :",null,null,null,null,null,"bars",null,null,null,false,false,false,false]
[null,null,null,null,"Calibre gicleur allure 2 :",null,null,null,null,null,"gal/h"]
[null,null,null,null,"Débit de fuel allure 2 :",null,{"$f":"IF(OR(Données!B5<>3,O95<>1),\"-\",ROUND(3.78*G111*(G110/6.89)^0.5,1))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5<>3,P95<>1),\"-\",ROUND(3.78*H111*(H110/6.89)^0.5,1))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5<>3,Q95<>1),\"-\",ROUND(3.78*I111*(I110/6.89)^0.5,1))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5<>3,R95<>1),\"-\",ROUND(3.78*J111*(J110/6.89)^0.5,1))","v":"-"},"litres/h"]
[null,null,null,null,"Puissance réelle allure 2 :",null,{"$f":"IF(OR(Données!B5<>3,O95<>1),\"-\",G112*Données!J5)","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5<>3,P95<>1),\"-\",H112*Données!J5)","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5<>3,Q95<>1),\"-\",I112*Données!J5)","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5<>3,R95<>1),\"-\",J112*Données!J5)","v":"-"},"kW"]
[null,null,null,null,"Rendement combustion allure 1 :",null,null,null,null,null,"%"]
[null,null,null,null,"Rendement combustion allure 2 :",null,null,null,null,null,"%"]
[null,null,null,null,"Puissance chaudière :",null,{"$f":"IF(OR(Données!B5<>3,O95<>1),\"-\",IF(O110,G113,IF(AND($P$82=1,G109<>0),G109,IF(O105,G105,\"données manquantes\"))))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5<>3,P95<>1),\"-\",IF(P110,H113,IF(AND($P$82=1,H109<>0),H109,IF(P105,H105,\"données manquantes\"))))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5<>3,Q95<>1),\"-\",IF(Q110,I113,IF(AND($P$82=1,I109<>0),I109,IF(Q105,I105,\"données manquantes\"))))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5<>3,R95<>1),\"-\",IF(R110,J113,IF(AND($P$82=1,J109<>0),J109,IF(R105,J105,\"données manquantes\"))))","v":"-"},"kW"]
[null,null,null,null,"Puissance brûleur allure 1 :",null,{"$f":"IF(OR(Données!B5<>3,O95<>1),\"-\",IF($P$82=1,G116,IF(O106,G109,IF(O105,G105*0.6,\"données manquantes\"))))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5<>3,P95<>1),\"-\",IF($P$82=1,H116,IF(P106,H109,IF(P105,H105*0.6,\"données manquantes\"))))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5<>3,Q95<>1),\"-\",IF($P$82=1,I116,IF(Q106,I109,IF(Q105,I105*0.6,\"données manquantes\"))))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5<>3,R95<>1),\"-\",IF($P$82=1,J116,IF(R106,J109,IF(R105,J105*0.6,\"données manquantes\"))))","v":"-"},"kW"]
[null,null,null,null,"Puissance brûleur allure 2 :",null,{"$f":"IF(OR(Données!B5<>3,O95<>1),\"-\",IF($P$82=1,\"-\",IF(O110,G113,IF(O105,G105,\"données manquantes\"))))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5<>3,P95<>1),\"-\",IF($P$82=1,\"-\",IF(P110,H113,IF(P105,H105,\"données manquantes\"))))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5<>3,Q95<>1),\"-\",IF($P$82=1,\"-\",IF(Q110,I113,IF(Q105,I105,\"données manquantes\"))))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5<>3,R95<>1),\"-\",IF($P$82=1,\"-\",IF(R110,J113,IF(R105,J105,\"données manquantes\"))))","v":"-"},"kW"]
[null,null,null,null,"Coeff perte arrêt à 70°C :",null,{"$f":"IF(OR(Données!B5<>3,O95<>1),\"-\",100*Données!B92*G116^Données!B93)","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5<>3,P95<>1),\"-\",100*Données!C92*H116^Données!C93)","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5<>3,Q95<>1),\"-\",100*Données!D92*I116^Données!D93)","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5<>3,R95<>1),\"-\",100*Données!E92*J116^Données!E93)","v":"-"},"%"]
[null,null,null,null,"Coeff perte arrêt majoré isolation :",null,{"$f":"IF(OR(Données!B5<>3,O95<>1),\"-\",IF(O98=1,G119,G119+$J$102))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5<>3,P95<>1),\"-\",IF(P98=1,H119,H119+$J$102))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5<>3,Q95<>1),\"-\",IF(Q98=1,I119,I119+$J$102))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5<>3,R95<>1),\"-\",IF(R98=1,J119,J119+$J$102))","v":"-"},"%"]
[null,null,null,null,"Clapet d'admission d'air :",null,null,null,null,null,null,null,null,null,2,2,2,2]
[]
[null,null,null,null,"Coeff perte arrêt majoré balayage :",null,{"$f":"IF(OR(Données!B5<>3,O95<>1),\"-\",IF(O121=1,G120+J101,G120))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5<>3,P95<>1),\"-\",IF(P121=1,H120+J101,H120))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5<>3,Q95<>1),\"-\",IF(Q121=1,I120+J101,I120))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5<>3,R95<>1),\"-\",IF(R121=1,J120+J101,J120))","v":"-"},"%"]
[null,null,null,null,"Coeff perte arrêt corr régulation T° :",null,{"$f":"IF(OR(Données!B5<>3,O95<>1),\"-\",G123*$I$86)","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5<>3,P95<>1),\"-\",H123*$I$86)","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5<>3,Q95<>1),\"-\",I123*$I$86)","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5<>3,R95<>1),\"-\",J123*$I$86)","v":"-"},"%"]
[null,null,null,null,"Coeff perte ambiance :",null,{"$f":"IF(OR(Données!B5<>3,O95<>1),\"-\",IF(O98=1,G120*$I$86,G120*$I$86*$J$103))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5<>3,P95<>1),\"-\",IF(P98=1,H120*$I$86,H120*$I$86*$J$103))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5<>3,Q95<>1),\"-\",IF(Q98=1,I120*$I$86,I120*$I$86*$J$103))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5<>3,R95<>1),\"-\",IF(R98=1,J120*$I$86,J120*$I$86*$J$103))","v":"-"},"%"]
[]
[null,null,null,null,"Chaudière à condensation :",null,null,null,null,null,null,null,null,null,2,2,2,2]
[]
[null,null,null,null,"Température moyenne de retour :",null,null,null,null,null,null,null,null,null,3,3,3,3]
[null,null,null,null,"Rendement de combustion par défaut :",null,{"$f":"IF(OR(Données!B5<>3,O95<>1),\"-\",IF(O127=2,\"-\",IF(O129=1,100,96)))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5<>3,P95<>1),\"-\",IF(P127=2,\"-\",IF(P129=1,100,96)))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5<>3,Q95<>1),\"-\",IF(Q127=2,\"-\",IF(Q129=1,100,96)))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5<>3,R95<>1),\"-\",IF(R127=2,\"-\",IF(R129=1,100,96)))","v":"-"},"%"]
[]
[]
[null,null,"Si brûleur gaz pulsé :",null,"Puissance nominale :",null,null,null,null,null,"kW",null,null,null,false,false,false,false]
[null,null,null,null,"Puissance brûleur allure 1 :",null,{"$f":"IF(OR(Données!B5=3,O95<>2),\"-\",IF($P$82=1,G133,IF($P$82=2,G133*0.6,\"données manquantes\")))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>2),\"-\",IF($P$82=1,H133,IF($P$82=2,H133*0.6,\"données manquantes\")))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>2),\"-\",IF($P$82=1,I133,IF($P$82=2,I133*0.6,\"données manquantes\")))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>2),\"-\",IF($P$82=1,J133,IF($P$82=2,J133*0.6,\"données manquantes\")))","v":"-"},"kW"]
[null,null,null,null,"Puissance brûleur allure 2 :",null,{"$f":"IF(OR(Données!B5=3,O95<>2),\"-\",IF($P$82=1,\"-\",IF($P$82=2,G133,\"données manquantes\")))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>2),\"-\",IF($P$82=1,\"-\",IF($P$82=2,H133,\"données manquantes\")))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>2),\"-\",IF($P$82=1,\"-\",IF($P$82=2,I133,\"données manquantes\")))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>2),\"-\",IF($P$82=1,\"-\",IF($P$82=2,J133,\"données manquantes\")))","v":"-"},"kW"]
[null,null,null,null,"Rendement combustion allure 1 :",null,null,null,null,null,"%"]
[null,null,null,null,"Rendement combustion allure 2 :",null,null,null,null,null,"%"]
[null,null,null,null,"Coeff perte arrêt à 70°C :",null,{"$f":"IF(OR(Données!B5=3,O95<>2),\"-\",100*Données!B92*G133^Données!B93)","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>2),\"-\",100*Données!C92*H133^Données!C93)","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>2),\"-\",100*Données!D92*I133^Données!D93)","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>2),\"-\",100*Données!E92*J133^Données!E93)","v":"-"},"%"]
[null,null,null,null,"Coeff perte arrêt majoré isolation :",null,{"$f":"IF(OR(Données!B5=3,O95<>2),\"-\",IF(O98=1,G138,G138+$J$102))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>2),\"-\",IF(P98=1,H138,H138+$J$102))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>2),\"-\",IF(Q98=1,I138,I138+$J$102))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>2),\"-\",IF(R98=1,J138,J138+$J$102))","v":"-"},"%"]
[null,null,null,null,"Clapet d'admission d'air :",null,null,null,null,null,null,null,null,null,1,1,2,2]
[null,null,null,null,"Coeff perte arrêt majoré balayage :",null,{"$f":"IF(OR(Données!B5=3,O95<>2),\"-\",IF(O140=1,G139+J101,G139))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>2),\"-\",IF(P140=1,H139+J101,H139))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>2),\"-\",IF(Q140=1,I139+J101,I139))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>2),\"-\",IF(R140=1,J139+J101,J139))","v":"-"},"%"]
[null,null,null,null,"Coeff perte arrêt corr régulation T° :",null,{"$f":"IF(OR(Données!B5=3,O95<>2),\"-\",G141*$I$86)","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>2),\"-\",H141*$I$86)","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>2),\"-\",I141*$I$86)","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>2),\"-\",J141*$I$86)","v":"-"},"%"]
[null,null,null,null,"Coeff perte ambiance :",null,{"$f":"IF(OR(Données!B5=3,O95<>2),\"-\",IF(O98=1,G139*$I$86,G139*$I$86*$J$103))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>2),\"-\",IF(P98=1,H139*$I$86,H139*$I$86*$J$103))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>2),\"-\",IF(Q98=1,I139*$I$86,I139*$I$86*$J$103))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>2),\"-\",IF(R98=1,J139*$I$86,J139*$I$86*$J$103))","v":"-"},"%"]
[]
[null,null,null,null,"Chaudière à condensation :",null,null,null,null,null,null,null,null,null,2,2,1,2]
[]
[null,null,null,null,"Température moyenne de retour :",null,null,null,null,null,null,null,null,null,3,3,3,3]
[null,null,null,null,"Rendement de combustion par défaut :",null,{"$f":"IF(OR(Données!B5=3,O95<>2),\"-\",IF(O145=2,\"-\",IF(O147=1,104,IF(O147=2,100,96))))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>2),\"-\",IF(P145=2,\"-\",IF(P147=1,104,IF(P147=2,100,96))))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>2),\"-\",IF(Q145=2,\"-\",IF(Q147=1,104,IF(Q147=2,100,96))))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>2),\"-\",IF(R145=2,\"-\",IF(R147=1,104,IF(R147=2,100,96))))","v":"-"},"%"]
[]
[]
[null,null,"Si brûleur gaz atmosphérique :",null,"Débit de gaz allure 1 :",null,null,null,null,null,"m³/h",null,null,null,false,false,false,false]
[null,null,null,null,"Débit de gaz allure 2 :",null,null,null,null,null,"m³/h",null,null,null,false,false,false,false]
[null,null,null,null,"Puissance brute allure 1 :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",G151*Données!J5)","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",H151*Données!J5)","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",I151*Données!J5)","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",J151*Données!J5)","v":"-"},"kW"]
[null,null,null,null,"Puissance brute allure 2 :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",G152*Données!J5)","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",H152*Données!J5)","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",I152*Données!J5)","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",J152*Données!J5)","v":"-"},"kW"]
[null,null,null,null,"Puissance brute allure 1 :",null,null,null,null,null,"kW",null,null,null,false,false,false,false]
[null,null,null,null,"Puissance brute allure 2 :",null,null,null,null,null,"kW",null,null,null,false,false,false,false]
[null,null,null,null,"Puissance nette allure 1 :",null,null,null,null,null,"kW",null,null,null,false,false,false,false]
[null,null,null,null,"Puissance nette allure 2 :",null,null,null,null,null,"kW",null,null,null,false,false,false,false]
[null,null,null,null,"Rend utile plaque allure 1 :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",IF(AND(O157,O151),100*G157/G153,IF(AND(O157,O155),100*G157/G155,\"Valeur par défaut\")))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",IF(AND(P157,P151),100*H157/H153,IF(AND(P157,P155),100*H157/H155,\"Valeur par défaut\")))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",IF(AND(Q157,Q151),100*I157/I153,IF(AND(Q157,Q155),100*I157/I155,\"Valeur par défaut\")))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",IF(AND(R157,R151),100*J157/J153,IF(AND(R157,R155),100*J157/J155,\"Valeur par défaut\")))","v":"-"},"%"]
[null,null,null,null,"Rend utile plaque allure 2 :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",IF($P$82=1,\"-\",IF(AND(O158,O151),100*G158/G154,IF(AND(O158,O155),100*G158/G156,\"Valeur par défaut\"))))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",IF($P$82=1,\"-\",IF(AND(P158,P151),100*H158/H154,IF(AND(P158,P155),100*H158/H156,\"Valeur par défaut\"))))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",IF($P$82=1,\"-\",IF(AND(Q158,Q151),100*I158/I154,IF(AND(Q158,Q155),100*I158/I156,\"Valeur par défaut\"))))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",IF($P$82=1,\"-\",IF(AND(R158,R151),100*J158/J154,IF(AND(R158,R155),100*J158/J156,\"Valeur par défaut\"))))","v":"-"},"%"]
[null,null,null,null,"Rend de comb par défaut allure 1 :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",INDEX(Données!$B$45:$B$47,MATCH(G97,Données!$A$45:$A$47,-1),1)-1)","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",INDEX(Données!$B$45:$B$47,MATCH(H97,Données!$A$45:$A$47,-1),1)-1)","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",INDEX(Données!$B$45:$B$47,MATCH(I97,Données!$A$45:$A$47,-1),1)-1)","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",INDEX(Données!$B$45:$B$47,MATCH(J97,Données!$A$45:$A$47,-1),1)-1)","v":"-"},"%"]
[null,null,null,null,"Rend de comb par défaut allure 2 :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",INDEX(Données!$B$45:$B$47,MATCH('Calcul du rendement'!G$97,Données!$A$45:$A$47,-1),1))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",INDEX(Données!$B$45:$B$47,MATCH('Calcul du rendement'!H$97,Données!$A$45:$A$47,-1),1))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",INDEX(Données!$B$45:$B$47,MATCH(I97,Données!$A$45:$A$47,-1),1))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",INDEX(Données!$B$45:$B$47,MATCH('Calcul du rendement'!J$97,Données!$A$45:$A$47,-1),1))","v":"-"},"%"]
[null,null,null,null,"Rend de comb allure 1 :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",IF(G159=\"Valeur par défaut\",G161,G159+G$168))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",IF(H159=\"Valeur par défaut\",H161,H159+H$168))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",IF(I159=\"Valeur par défaut\",I161,I159+I$168))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",IF(J159=\"Valeur par défaut\",J161,J159-J$168))","v":"-"},"%"]
[null,null,null,null,"Rend de comb allure 2 :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",IF($P$82=1,\"-\",IF(G160=\"Valeur par défaut\",G162,G160+G$168)))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",IF($P$82=1,\"-\",IF(H160=\"Valeur par défaut\",H162,H160+H$168)))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",IF($P$82=1,\"-\",IF(I160=\"Valeur par défaut\",I162,I160+I$168)))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",IF($P$82=1,\"-\",IF(J160=\"Valeur par défaut\",J162,J160-J$168)))","v":"-"},"%"]
[null,null,null,null,"Puissance chaudière :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",IF(O152,G154,IF(O156,G156,IF($P$82=1,IF(O151,G153,IF(O155,G155,\"données manquantes\"))))))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",IF(P152,H154,IF(P156,H156,IF($P$82=1,IF(P151,H153,IF(P155,H155,\"données manquantes\"))))))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",IF(Q152,I154,IF(Q156,I156,IF($P$82=1,IF(Q151,I153,IF(Q155,I155,\"données manquantes\"))))))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",IF(R152,J154,IF(R156,J156,IF($P$82=1,IF(R151,J153,IF(R155,J155,\"données manquantes\"))))))","v":"-"},"kW"]
[null,null,null,null,"Puissance brûleur allure 1 :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",IF($P$82=1,G165,IF(O151,G153,IF(O155,G155,\"-\"))))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",IF($P$82=1,H165,IF(P151,H153,IF(P155,H155,\"-\"))))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",IF($P$82=1,I165,IF(Q151,I153,IF(Q155,I155,\"-\"))))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",IF($P$82=1,J165,IF(R151,J155,IF(R155,J155,\"-\"))))","v":"-"},"kW"]
[null,null,null,null,"Puissance brûleur allure 2 :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",IF($P$82=1,\"-\",IF(O152,G154,IF(O156,G156,\"données manquantes\"))))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",IF($P$82=1,\"-\",IF(P152,H154,IF(P156,H156,\"données manquantes\"))))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",IF($P$82=1,\"-\",IF(Q152,I154,IF(Q156,I156,\"données manquantes\"))))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",IF($P$82=1,\"-\",IF(R152,J154,IF(R156,J156,\"données manquantes\"))))","v":"-"},"kW"]
[null,null,null,null,"Coeff perte arrêt à 70°C :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",(100*Données!B92*G165^Données!B93)+0.7)","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",(100*Données!C92*H165^Données!C93)+0.7)","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",(100*Données!D92*I165^Données!D93)+0.7)","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",(100*Données!E92*J165^Données!E93)+0.7)","v":"-"},"%"]
[null,null,null,null,"Coeff perte arrêt majoré isolation :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",IF(O98=1,G168,G168+$J$102))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",IF(P98=1,H168,H168+$J$102))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",IF(Q98=1,I168,I168+$J$102))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",IF(R98=1,J168,J168+$J$102))","v":"-"},"%"]
[null,null,null,null,"Coeff perte arrêt corr régulation T° :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",G169*$I$86)","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",H169*$I$86)","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",I169*$I$86)","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",J169*$I$86)","v":"-"},"%"]
[null,null,null,null,"Coeff perte ambiance :",null,{"$f":"IF(OR(Données!B5=3,O95<>3),\"-\",IF(O98=1,G170,G170*$J$103))","v":"-"},{"$f":"IF(OR(H94=\"-\",Données!B5=3,P95<>3),\"-\",IF(P98=1,H170,H170*$J$103))","v":"-"},{"$f":"IF(OR(I94=\"-\",Données!B5=3,Q95<>3),\"-\",IF(Q98=1,I170,I170*$J$103))","v":"-"},{"$f":"IF(OR(J94=\"-\",Données!B5=3,R95<>3),\"-\",IF(R98=1,J170,J170*$J$103))","v":"-"},"%"]
[]
[]
[null,"RECAPITULATIF",null,null,null,null,"Chaudière 1",{"$f":"IF($E$64<2,\"-\",\"Chaudière 2\")","v":"-"},{"$f":"IF($E$64<3,\"-\",\"Chaudière 3\")","v":"-"},{"$f":"IF($E$64<4,\"-\",\"Chaudière 4\")","v":"-"},"Total"]
[null,null,null,null,"Puissance :",null,{"$f":"IF(AND(O95=1,G94=\"chaudière 1\"),G116,IF(AND(O95=2,G94=\"chaudière 1\"),G133,IF(AND(O95=3,G94=\"chaudière 1\"),G165,IF(G94=\"-\",\"-\",\"données manquantes\"))))","v":"-"},{"$f":"IF(AND(P95=1,H94=\"chaudière 2\"),H116,IF(AND(P95=2,H94=\"chaudière 2\"),H133,IF(AND(P95=3,H94=\"chaudière 2\"),H165,IF(H94=\"-\",\"-\",\"données manquantes\"))))","v":"-"},{"$f":"IF(AND(Q95=1,I94=\"chaudière 3\"),I116,IF(AND(Q95=2,I94=\"chaudière 3\"),I133,IF(AND(Q95=3,I94=\"chaudière 3\"),I165,IF(I94=\"-\",\"-\",\"données manquantes\"))))","v":"-"},{"$f":"IF(AND(R95=1,J94=\"chaudière 4\"),J116,IF(AND(R95=2,J94=\"chaudière 4\"),J133,IF(AND(R95=3,J94=\"chaudière 4\"),J165,IF(J94=\"-\",\"-\",\"données manquantes\"))))","v":"-"},{"$f":"SUM(G175:J175)","v":0},"kW"]
[null,null,null,null,"Puissance brûleur allure 1 :",null,{"$f":"IF(AND(O95=1,G94=\"chaudière 1\"),G117,IF(AND(O95=2,G94=\"chaudière 1\"),G134,IF(AND(O95=3,G94=\"chaudière 1\"),G166,\"-\")))","v":"-"},{"$f":"IF(AND(P95=1,H94=\"chaudière 2\"),H117,IF(AND(P95=2,H94=\"chaudière 2\"),H134,IF(AND(P95=3,H94=\"chaudière 2\"),H166,\"-\")))","v":"-"},{"$f":"IF(AND(Q95=1,I94=\"chaudière 3\"),I117,IF(AND(Q95=2,I94=\"chaudière 3\"),I134,IF(AND(Q95=3,I94=\"chaudière 3\"),I166,\"-\")))","v":"-"},{"$f":"IF(AND(R95=1,J94=\"chaudière 4\"),J117,IF(AND(R95=2,J94=\"chaudière 4\"),J134,IF(AND(R95=3,J94=\"chaudière 4\"),J166,\"-\")))","v":"-"},"kW"]
[null,null,null,null,"Puissance brûleur allure 2 :",null,{"$f":"IF(AND(O95=1,G94=\"chaudière 1\"),G118,IF(AND(O95=2,G94=\"chaudière 1\"),G135,IF(AND(O95=3,G94=\"chaudière 1\"),G167,IF($P$82=1,\"-\",\"données manquantes\"))))","v":"-"},{"$f":"IF(AND(P95=1,H94=\"chaudière 2\"),H118,IF(AND(P95=2,H94=\"chaudière 2\"),H135,IF(AND(P95=3,H94=\"chaudière 2\"),H167,IF($P$82=1,\"-\",\"-\"))))","v":"-"},{"$f":"IF(AND(Q95=1,I94=\"chaudière 3\"),I118,IF(AND(Q95=2,I94=\"chaudière 3\"),I135,IF(AND(Q95=3,I94=\"chaudière 3\"),I167,IF($P$82=1,\"-\",\"-\"))))","v":"-"},{"$f":"IF(AND(R95=1,J94=\"chaudière 4\"),J118,IF(AND(R95=2,J94=\"chaudière 4\"),J135,IF(AND(R95=3,J94=\"chaudière 4\"),J167,IF($P$82=1,\"-\",\"-\"))))","v":"-"},"kW"]
[null,null,null,null,"Rendement de comb allure 1 :",null,{"$f":"IF(AND(O95=1,G94=\"chaudière 1\"),IF(O127=1,G130,IF(AND($P$82=2,G114=\"\"),G115+2,G114)),IF(AND(O95=2,G94=\"chaudière 1\"),IF(O145=1,G148,IF(AND($P$82=2,G136=\"\"),G137+2,G136)),IF(AND(O95=3,G94=\"chaudière 1\"),IF(O157,G163,G161),\"-\")))","v":0},{"$f":"IF(AND(P95=1,H94=\"chaudière 2\"),IF(P127=1,H130,IF(AND($P$82=2,H114=\"\"),H115+2,H114)),IF(AND(P95=2,H94=\"chaudière 2\"),IF(P145=1,H148,IF(AND($P$82=2,H136=\"\"),H137+2,H136)),IF(AND(P95=3,H94=\"chaudière 2\"),IF(P157,H163,H161),\"-\")))","v":"-"},{"$f":"IF(AND(Q95=1,I94=\"chaudière 3\"),IF(Q127=1,I130,IF(AND($P$82=2,I114=\"\"),I115+2,I114)),IF(AND(Q95=2,I94=\"chaudière 3\"),IF(Q145=1,I148,IF(AND($P$82=2,I136=\"\"),I137+2,I136)),IF(AND(Q95=3,I94=\"chaudière 3\"),IF(Q157,I163,I161),\"-\")))","v":"-"},{"$f":"IF(AND(R95=1,J94=\"chaudière 4\"),IF(R127=1,J130,IF(AND($P$82=2,J114=\"\"),J115+2,J114)),IF(AND(R95=2,J94=\"chaudière 4\"),IF(R145=1,J148,IF(AND($P$82=2,J136=\"\"),J137+2,J136)),IF(AND(R95=3,J94=\"chaudière 4\"),IF(R157,J163,J161),\"-\")))","v":"-"},"%"]
[null,null,null,null,"Rendement de comb allure 2 :",null,{"$f":"IF($P$82=1,\"-\",IF(AND(O95=1,G94=\"chaudière 1\"),IF(O127=1,G130,G115),IF(AND(O95=2,G94=\"chaudière 1\"),IF(O145=1,G148,G137),IF(AND(O95=3,G94=\"chaudière 1\"),IF(O158,G164,G162),\"données manquantes\"))))","v":"-"},{"$f":"IF($P$82=1,\"-\",IF(AND(P95=1,H94=\"chaudière 2\"),IF(P127=1,H130,H115),IF(AND(P95=2,H94=\"chaudière 2\"),IF(P145=1,H148,H137),IF(AND(P95=3,H94=\"chaudière 2\"),IF(P158,H164,H162),\"-\"))))","v":"-"},{"$f":"IF($P$82=1,\"-\",IF(AND(Q95=1,I94=\"chaudière 3\"),IF(Q127=1,I130,I115),IF(AND(Q95=2,I94=\"chaudière 3\"),IF(Q145=1,I148,I137),IF(AND(Q95=3,I94=\"chaudière 3\"),IF(Q158,I164,I162),\"-\"))))","v":"-"},{"$f":"IF($P$82=1,\"-\",IF(AND(R95=1,J94=\"chaudière 4\"),IF(R127=1,J130,J115),IF(AND(R95=2,J94=\"chaudière 4\"),IF(R145=1,J148,J137),IF(AND(R95=3,J94=\"chaudière 4\"),IF(R158,J164,J162),\"-\"))))","v":"-"},"%"]
[null,null,null,null,"Rendement utile allure 1 :",null,{"$f":"IF(G94=\"-\",\"-\",G178-G183)","v":{"$error":"#VALUE!"}},{"$f":"IF(H94=\"-\",\"-\",H178-H183)","v":"-"},{"$f":"IF(I94=\"-\",\"-\",I178-I183)","v":"-"},{"$f":"IF(J94=\"-\",\"-\",J178-J183)","v":"-"},"%"]
[null,null,null,null,"Rendement utile allure 2 :",null,{"$f":"IF($P$82=1,\"-\",G179-G183)","v":"-"},{"$f":"IF(H174=\"-\",\"-\",IF($P$82=1,\"-\",H179-H183))","v":"-"},{"$f":"IF(I174=\"-\",\"-\",IF($P$82=1,\"-\",I179-I183))","v":"-"},{"$f":"IF(J174=\"-\",\"-\",IF($P$82=1,\"-\",J179-J183))","v":"-"},"%"]
[null,null,null,null,"Coeff perte arrêt :",null,{"$f":"IF(AND(O95=1,G94=\"chaudière 1\"),G123,IF(AND(O95=2,G94=\"chaudière 1\"),G141,IF(AND(O95=3,G94=\"chaudière 1\"),G170,\"-\")))","v":"-"},{"$f":"IF(AND(P95=1,H94=\"chaudière 2\"),H123,IF(AND(P95=2,H94=\"chaudière 2\"),H141,IF(AND(P95=3,H94=\"chaudière 2\"),H170,\"-\")))","v":"-"},{"$f":"IF(AND(Q95=1,I94=\"chaudière 3\"),I123,IF(AND(Q95=2,I94=\"chaudière 3\"),I141,IF(AND(Q95=3,I94=\"chaudière 3\"),I170,\"-\")))","v":"-"},{"$f":"IF(AND(R95=1,J94=\"chaudière 4\"),J123,IF(AND(R95=2,J94=\"chaudière 4\"),J141,IF(AND(R95=3,J94=\"chaudière 4\"),J170,\"-\")))","v":"-"},"%"]
[null,null,null,null,"Coeff perte ambiance :",null,{"$f":"IF(AND(O95=1,G94=\"chaudière 1\"),G125,IF(AND(O95=2,G94=\"chaudière 1\"),G143,IF(AND(O95=3,G94=\"chaudière 1\"),G171,\"-\")))","v":"-"},{"$f":"IF(AND(P95=1,H94=\"chaudière 2\"),H125,IF(AND(P95=2,H94=\"chaudière 2\"),H143,IF(AND(P95=3,H94=\"chaudière 2\"),H171,\"-\")))","v":"-"},{"$f":"IF(AND(Q95=1,I94=\"chaudière 3\"),I125,IF(AND(Q95=2,I94=\"chaudière 3\"),I143,IF(AND(Q95=3,I94=\"chaudière 3\"),I171,\"-\")))","v":"-"},{"$f":"IF(AND(R95=1,J94=\"chaudière 4\"),J125,IF(AND(R95=2,J94=\"chaudière 4\"),J143,IF(AND(R95=3,J94=\"chaudière 4\"),J171,\"-\")))","v":"-"},"%"]
[]
[]
[null,"Calcul du temps de fonctionnement des brûleurs pour chaque allure"]
[]
[null,"Répartition des puissances :"]
[]
[null,null,null,null,null,"Puissances installées [kW] "]
[null,null,null,null,"Chaudière 1",{"$f":"IF($E$64<2,\"-\",\"Chaudière 2\")","v":"-"},{"$f":"IF($E$64<3,\"-\",\"Chaudière 3\")","v":"-"},{"$f":"IF($E$64<4,\"-\",\"Chaudière 4\")","v":"-"}]
[null,null,null,"Allure 1 du brûleur",{"$f":"G261","v":{"$error":"#VALUE!"}},0,0,0]
[null,null,null,{"$f":"IF(Données!B27=2,\"Allure 2 du brûleur\",\"-\")","v":"-"},0,0,0,0]
[]
[null,null,null,null,null,"Energie consommée",null,"Durée de fonctionnement "]
[null,null,"Allure",null,null,"par chaque allure ",null,"du brûleur à chaque allure"]
[null,null,null,null,null,"[kWh/an]",null,"[heures/an]"]
[]
[null,null,{"$f":"B349","v":"- Chaudière 1"},null,null,{"$f":"IF(Données!$B$33=1,INDEX(C349:J349,1,Données!$B$27),INDEX(C349:J349,1,'Calcul du rendement'!F264))","v":49605},null,{"$f":"IF(Données!$B$33=1,INDEX(C362:J362,1,Données!$B$27),INDEX(C362:J362,1,'Calcul du rendement'!F264))","v":{"$error":"#VALUE!"}}]
[null,null,"- -",null,null,{"$f":"IF(C200=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C350:J350,1,Données!$B$27),INDEX(C350:J350,1,'Calcul du rendement'!F264)))","v":""},null,{"$f":"IF(C200=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C363:J363,1,Données!$B$27),INDEX(C363:J363,1,'Calcul du rendement'!F264)))","v":""}]
[null,null,"- -",null,null,{"$f":"IF(C201=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C351:J351,1,Données!$B$27),INDEX(C351:J351,1,'Calcul du rendement'!F264)))","v":""},null,{"$f":"IF(C201=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C364:J364,1,Données!$B$27),INDEX(C364:J364,1,'Calcul du rendement'!F264)))","v":""}]
[null,null,"- -",null,null,{"$f":"IF(C202=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C352:J352,1,Données!$B$27),INDEX(C352:J352,1,'Calcul du rendement'!F264)))","v":""},null,{"$f":"IF(C202=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C365:J365,1,Données!$B$27),INDEX(C365:J365,1,'Calcul du rendement'!F264)))","v":""}]
[null,null,"- -",null,null,{"$f":"IF(C203=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C353:J353,1,Données!$B$27),INDEX(C353:J353,1,'Calcul du rendement'!F264)))","v":""},null,{"$f":"IF(C203=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C366:J366,1,Données!$B$27),INDEX(C366:J366,1,'Calcul du rendement'!F264)))","v":""}]
[null,null,"- -",null,null,{"$f":"IF(C204=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C354:J354,1,Données!$B$27),INDEX(C354:J354,1,'Calcul du rendement'!F264)))","v":""},null,{"$f":"IF(C204=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C367:J367,1,Données!$B$27),INDEX(C367:J367,1,'Calcul du rendement'!F264)))","v":""}]
[null,null,"- -",null,null,{"$f":"IF(C205=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C355:J355,1,Données!$B$27),INDEX(C355:J355,1,'Calcul du rendement'!F264)))","v":""},null,{"$f":"IF(C205=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C368:J368,1,Données!$B$27),INDEX(C368:J368,1,'Calcul du rendement'!F264)))","v":""}]
[null,null,"- -",null,null,{"$f":"IF(C206=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C356:J356,1,Données!$B$27),INDEX(C356:J356,1,'Calcul du rendement'!F264)))","v":""},null,{"$f":"IF(C206=\"- -\",\"\",IF(Données!$B$33=1,INDEX(C369:J369,1,Données!$B$27),INDEX(C369:J369,1,'Calcul du rendement'!F264)))","v":""}]
[]
[null,null,null,null,null,"Durée d'utilisation de chaque chaudière"]
[null,null,"Chaudière",null,null,"[heures/an]"]
[]
[null,null,"- Chaudière 1",null,null,{"$f":"MAX(H421:H428)","v":5808}]
[null,null,{"$f":"IF(E64>1,\"- Chaudière 2\",\"\")","v":""},null,null,{"$f":"IF(E64>1,IF(Données!B33<3,F211,LARGE(H421:H428,2)),\"\")","v":""}]
[null,null,{"$f":"IF(E64>2,\"- Chaudière 3\",\"\")","v":""},null,null,{"$f":"IF(E64>2,IF(Données!B33<3,F211,LARGE(H421:H428,3)),\"\")","v":""}]
[null,null,{"$f":"IF(E64>3,\"- Chaudière 4\",\"\")","v":""},null,null,{"$f":"IF(E64>3,IF(Données!B33<3,F211,LARGE(H421:H428,4)),\"\")","v":""}]
[null,null,null,null,null,null," "]
[null,null,"On fait l'hypothèse que, dans le cas d'une combinaison de chaudières multiples, la "]
[null,null,"première chaudière de la cascade est en permanence irriguée. Les autres chaudières à "]
[null,null,"l'arrêt peuvent être isolées hydrauliquement de l'installation."]
[]
[null,"Facteur de charge de l'installation (surdimensionnement)"]
[]
[null,"Le facteur de charge est de :",null,null,{"$f":"100*(F28/K175)/E59","v":{"$error":"#DIV/0!"}},"%"]
[null,null,null,"Soit :",{"$f":"F28/K175","v":{"$error":"#DIV/0!"}},"heures de fonctionnement à puissance nominale"]
[]
[null,"Rendement saisonnier de l'installation de production de chaleur"]
[]
[null,"Rendement saisonnier :",null,{"$f":"ROUND(IF(Données!B33=3,(D429-E429-M429)/D429*100,(D429-E429-N429)/D429*100),1)","v":{"$error":"#VALUE!"}},"%","(= [consommation - pertes de combustion - pertes à l'arrêt] / consommation)"]
[]
[]
[null,"Economie suite à l'amélioration du rendement saisonnier"]
[]
[null,"Encodez ici le rendement saisonnier calculé avant amélioration :",null,null,null,null,null,"%"]
[]
[null,"Encodez ici le rendement saisonnier calculé après amélioration :",null,null,null,null,null,"%"]
[]
[null,"Gain énergétique :",null,{"$f":"IF(OR(G232=\"\",G234=\"\"),\"\",ROUND(F26*(1-G232/G234),0))","v":""},{"$f":"Données!C11","v":"kWh de gaz PCS"}]
[]
[null,"Coût unitaire du combustible :",null,0.5,{"$f":"IF(Données!B11=1,\"€/litre de mazout\",IF(Données!B11=2,\"€/m³ de gaz\",\"€/kWh de gaz\"))","v":"€/kWh de gaz"}]
[]
[null,"Gain financier :",null,{"$f":"IF(D236=\"\",\"\",ROUND(D236*D238,0))","v":""},"€/an"]
[]
[null,"Economie suite au remplacement complet de l'installation de production de chaleur"]
[]
[null,"Si remplacement complet de l'installation de chauffage :"]
[]
[null,null,"- par une installation fuel ou gaz traditionnelle à brûleur pulsé (rendement saisonnier escompté = ..93..%), l'économie serait de :",null,null,null,null,null,{"$f":"IF(OR(F26=\"\",D227=\"\",D227>93),\"-\",ROUND(F26*(1-D227/93),0))","v":{"$error":"#VALUE!"}},{"$f":"Données!C11","v":"kWh de gaz PCS"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(I246=\"-\",\"-\",IF(D238=\"\",\"Précisez le prix combustible\",ROUND(I246*D238,0)))","v":{"$error":"#VALUE!"}},"€/an"]
[]
[null,null,"- par une installation mazout à condensation à brûleur pulsé (rendement saisonnier escompté = ..98..%), l'économie serait de :",null,null,null,null,null,{"$f":"IF(Données!B5<3,\"-\",IF(OR(F26=\"\",D227=\"\",D227>98),\"-\",ROUND(F26*(1-D227/98),0)))","v":"-"},"litres de mazout"]
[null,null,null,null,null,null,null,null,{"$f":"IF(I249=\"-\",\"-\",IF(D238=\"\",\"Précisez le prix combustible\",ROUND(I249*D238,0)))","v":"-"},"€/an"]
[]
[null,null,"- par une installation gaz à condensation à brûleur modulant (rendement saisonnier escompté = ..102..%), l'économie serait de :",null,null,null,null,null,{"$f":"IF(OR(F26=\"\",D227=\"\",D227>102),\"-\",ROUND(F26*(1-D227/102),0))","v":{"$error":"#VALUE!"}},{"$f":"Données!C11","v":"kWh de gaz PCS"}]
[null,null,null,null,null,null,null,null,{"$f":"IF(I252=\"-\",\"-\",IF(D238=\"\",\"Précisez le prix combustible\",ROUND(I252*D238,0)))","v":{"$error":"#VALUE!"}},"€/an"]
[]
[]
[null,"Calculs des pertes de combustion et des pertes à l'arrêt pour le calcul du rendement saisonnier"]
[]
[]
[null,"Puissance totale installée",null,{"$f":"ROUND(K175,0)","v":0},"kW",null,"Puissances installées [kW] "]
[null,"Nombre de chaudières:",null,{"$f":"E64","v":1},null,null,"Chaudière 1",{"$f":"IF(D260<2,\"-\",\"Chaudière 2\")","v":"-"},{"$f":"IF(D260<3,\"-\",\"Chaudière 3\")","v":"-"},{"$f":"IF(D260<4,\"-\",\"Chaudière 4\")","v":"-"}]
[null,null,null,null,null,"Allure 1 du brûleur",{"$f":"IF(Données!B33=1,IF(Données!B27=2,ROUND(D259*0.6,0),D259),IF(P82=1,ROUND(G176,0),ROUND(G176,0)))","v":{"$error":"#VALUE!"}},{"$f":"IF($D260>1,IF(Données!B33=1,0,IF(P82=1,ROUND(H176,0),ROUND(H176,0))),0)","v":0},{"$f":"IF($D260>2,IF(Données!B33=1,0,IF(P82=1,ROUND(I176,0),ROUND(I176,0))),0)","v":0},{"$f":"IF($D260>3,IF(Données!B33=1,0,IF(P82=1,ROUND(J176,0),ROUND(J176,0))),0)","v":0}]
[null,null,null,null,null,{"$f":"IF(Données!$B$27=2,\"Allure 2 du brûleur\",\"-\")","v":"-"},{"$f":"IF(Données!B33=1,IF(Données!B27=1,0,D259),IF(P82=1,0,ROUND(G177,0)))","v":0},{"$f":"IF($D260>1,IF(Données!B33=1,0,IF(P82=1,0,ROUND(H177,0))),0)","v":0},{"$f":"IF($D260>2,IF(Données!B33=1,0,IF(P82=1,0,ROUND(I177,0))),0)","v":0},{"$f":"IF($D260>3,IF(Données!B33=1,0,IF(P82=1,0,ROUND(J177,0))),0)","v":0}]
[]
[null,"Choix de la combinaison chaudière + brûleur :",null,null,null,{"$f":"(D260-1)*2+Données!B27","v":1}]
[null,"Ordre d'enclenchement des étages de puissance :",null,null,null,"(chaudière 1 allure 1) - (chaudière 1 allure 2) - (chaudière 2 allure 1) - (chaudière 2 allure 2) - ..."]
[]
[]
[null,"CADRE 1"]
[null,null,"Présentation des différentes"]
[null,null,"combinaisons chaudière/brûleur"]
[null,"Combinaison 1","= 1 chaudière 1 allure"]
[null,"Combinaison 2","= 1 chaudière 2 allures"]
[null,"Combinaison 3","= 2 chaudières 1 allure"]
[null,"Combinaison 4","= 2 chaudières 2 allures"]
[null,"Combinaison 5","= 3 chaudières 1 allure"]
[null,"Combinaison 6","= 3 chaudières 2 allures"]
[null,"Combinaison 7","= 4 chaudières 1 allure"]
[null,"Combinaison 8","= 4 chaudières 2 allures"]
[]
[]
[null,"CADRE 2",null,null,null,null,null,null,null,null,null,"CADRE 3"]
[null,"Puissance de chacune des allures de chaque chaudière - 8 combinaisons possibles",null,null,null,null,null,null,null,null,null,null,"Puissance brute"]
[null,null,"Comb1","Comb2","Comb3","Comb4","Comb5","Comb6","Comb7","Comb8",null,null,"de chaque brûleur"]
[null,1,{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},null,"1.",{"$f":"INDEX(C284:J284,1,$F$264)","v":{"$error":"#VALUE!"}},"kW"]
[null,2,0,{"$f":"G262","v":0},{"$f":"H261","v":0},{"$f":"G262","v":0},{"$f":"H261","v":0},{"$f":"G262","v":0},{"$f":"H261","v":0},{"$f":"G262","v":0},null,"2.",0,"kW"]
[null,3,{"$f":"C285","v":0},0,0,{"$f":"H261","v":0},{"$f":"I261","v":0},{"$f":"H261","v":0},{"$f":"I261","v":0},{"$f":"H261","v":0},null,"3.",0,"kW"]
[null,4,{"$f":"C286","v":0},{"$f":"D286","v":0},0,{"$f":"H262","v":0},0,{"$f":"H262","v":0},{"$f":"J261","v":0},{"$f":"H262","v":0},null,"4.",0,"kW"]
[null,5,{"$f":"C287","v":0},0,0,0,0,{"$f":"I261","v":0},0,{"$f":"I261","v":0},null,"5.",0,"kW"]
[null,6,{"$f":"C288","v":0},0,0,0,0,{"$f":"I262","v":0},0,{"$f":"I262","v":0},null,"6.",0,"kW"]
[null,7,0,0,0,0,0,0,0,{"$f":"J261","v":0},null,"7.",0,"kW"]
[null,8,0,0,0,0,0,0,0,{"$f":"J262","v":0},null,"8.",0,"kW"]
[]
[null,"CADRE 4",null,null,null,null,null,null,null,null,null,"CADRE 5"]
[null,"Succession des puissances mises en œuvre pour satisfaire aux besoins - 8 combinaisons possibles",null,null,null,null,null,null,null,null,null,null,"Succession des puissances mises en"]
[null,null,"Comb1","Comb2","Comb3","Comb4","Comb5","Comb6","Comb7","Comb8",null,null,"oeuvre en fonction des besoins"]
[null,1,{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},{"$f":"G261","v":{"$error":"#VALUE!"}},null,"1.",{"$f":"INDEX(C296:J296,1,$F$264)","v":{"$error":"#VALUE!"}},"kW"]
[null,2,{"$f":"C296","v":{"$error":"#VALUE!"}},{"$f":"G262","v":0},{"$f":"G261+H261","v":{"$error":"#VALUE!"}},{"$f":"G262","v":0},{"$f":"G261+H261","v":{"$error":"#VALUE!"}},{"$f":"G262","v":0},{"$f":"G261+H261","v":{"$error":"#VALUE!"}},{"$f":"G262","v":0},null,"2.",{"$error":"#VALUE!"},"kW"]
[null,3,{"$error":"#VALUE!"},{"$f":"D297","v":0},{"$error":"#VALUE!"},{"$f":"G262+H261","v":0},{"$f":"G261+H261+I261","v":{"$error":"#VALUE!"}},{"$f":"G262+H261","v":0},{"$f":"G261+H261+I261","v":{"$error":"#VALUE!"}},{"$f":"G262+H261","v":0},null,"3.",{"$error":"#VALUE!"},"kW"]
[null,4,{"$error":"#VALUE!"},0,{"$error":"#VALUE!"},{"$f":"G262+H262","v":0},{"$f":"G298","v":{"$error":"#VALUE!"}},{"$f":"G262+H262","v":0},{"$f":"G261+H261+I261+J261","v":{"$error":"#VALUE!"}},{"$f":"G262+H262","v":0},null,"4.",{"$error":"#VALUE!"},"kW"]
[null,5,{"$error":"#VALUE!"},0,{"$error":"#VALUE!"},{"$f":"F299","v":0},{"$f":"G299","v":{"$error":"#VALUE!"}},{"$f":"G262+H262+I261","v":0},{"$f":"I299","v":{"$error":"#VALUE!"}},{"$f":"G262+H262+I261","v":0},null,"5.",{"$error":"#VALUE!"},"kW"]
[null,6,{"$error":"#VALUE!"},0,{"$error":"#VALUE!"},{"$f":"F300","v":0},{"$f":"G300","v":{"$error":"#VALUE!"}},{"$f":"G262+H262+I262","v":0},{"$f":"I300","v":{"$error":"#VALUE!"}},{"$f":"G262+H262+I262","v":0},null,"6.",{"$error":"#VALUE!"},"kW"]
[null,7,{"$error":"#VALUE!"},0,{"$error":"#VALUE!"},{"$f":"F301","v":0},{"$f":"G301","v":{"$error":"#VALUE!"}},{"$f":"H301","v":0},{"$f":"I301","v":{"$error":"#VALUE!"}},{"$f":"G262+H262+I262+J261","v":0},null,"7.",{"$error":"#VALUE!"},"kW"]
[null,8,{"$error":"#VALUE!"},0,{"$error":"#VALUE!"},{"$f":"F302","v":0},{"$f":"G302","v":{"$error":"#VALUE!"}},{"$f":"H302","v":0},{"$f":"I302","v":{"$error":"#VALUE!"}},{"$f":"G262+H262+I262+J262","v":0},null,"8.",{"$error":"#VALUE!"},"kW"]
[]
[null,"CADRE 6"]
[null,"Expression écrite des différentes combinaisons chaudière/brûleur"]
[null,null,"Comb1","Comb2","Comb3","Comb4","Comb5","Comb6","Comb7","Comb8"]
[null,1,"- Chaudière 1","- Chaudière 1, allure 1","- Chaudière 1","- Chaudière 1, allure 1","- Chaudière 1","- Chaudière 1, allure 1","- Chaudière 1","- Chaudière 1, allure 1"]
[null,2,"- -","- Chaudière 1, allure 2","- Chaudière 2","- Chaudière 1, allure 2","- Chaudière 2","- Chaudière 1, allure 2","- Chaudière 2","- Chaudière 1, allure 2"]
[null,3,"- -","- -","- -","- Chaudière 2, allure 1","- Chaudière 3","- Chaudière 2, allure 1","- Chaudière 3","- Chaudière 2, allure 1"]
[null,4,"- -","- -","- -","- Chaudière 2, allure 2","- -","- Chaudière 2, allure 2","- Chaudière 4","- Chaudière 2, allure 2"]
[null,5,"- -","- -","- -","- -","- -","- Chaudière 3, allure 1","- -","- Chaudière 3, allure 1"]
[null,6,"- -","- -","- -","- -","- -","- Chaudière 3, allure 2","- -","- Chaudière 3, allure 2"]
[null,7,"- -","- -","- -","- -","- -","- -","- -","- Chaudière 4, allure 1"]
[null,8,"- -","- -","- -","- -","- -","- -","- -","- Chaudière 4, allure 2"]
[]
[]
[null,"CADRE 7",null,null,null,"CADRE 8",null,null,"CADRE 9",null,null,"CADRE 10",null,null,null,"CADRE 11"]
[null,"Etablissement de la monotone de chaleur",null,null,null,"Etablissement de la courbe de Gauss des puissances",null,null,"Consommation par tranche de P en %",null,null,"Etablissement de la monotone de puissance",null,null,null,"Consommation par tranche de P en kW"]
[null,{"$f":"IF(G17=\"UCCLE\",'Fichier météo UCCLE'!$Y$8782,'Fichier météo StHubert'!$Y$8782)","v":5600},"h    à P > à ",0,"% de Pbesoin",{"$f":"(B320-B321)*(D320+D321)/2","v":390},{"$f":"F320/F$331","v":1.4211274277593558E-3},"du temps à P = 5%",{"$f":"G320*$F$28","v":70.502131691141642},"kWh pour la tranche","de 0 à 10 % de P",{"$f":"ROUND((B320+B321)/2,0)","v":5561},"h    à P > à ",{"$f":"I320/(B320-B321)","v":0.90387348321976468},"kW - ligne 1",{"$f":"I320/2","v":35.251065845570821},"de P 0% à P 5%"]
[null,{"$f":"IF(G18=\"UCCLE\",'Fichier météo UCCLE'!$X$8782,'Fichier météo StHubert'!$X$8782)","v":5522},"h    à P > à ",10,"% de Pbesoin",3945,1.4375250519258099E-2,"du temps à P = 15%",713.15617826039431,"kWh pour la tranche","de 10 à 20 % de P",5391,"h    à P > à ",{"$f":"I321/(B321-B322)","v":2.7116204496592942},"kW - ligne 2",{"$f":"(L320-L321)*(N321+N320)/2","v":307.31698429471999},"de P 5% à  P 15%"]
[null,{"$f":"IF(G19=\"UCCLE\",'Fichier météo UCCLE'!$W$8782,'Fichier météo StHubert'!$W$8782)","v":5259},"h    à P > à ",20,"% de Pbesoin",14350,5.2290201508581421E-2,"du temps à P = 25%",2594.1168968407242,"kWh pour la tranche","de 20 à 30 % de P",4972,"h    à P > à ",{"$f":"IF(L322<>0,I322/(B322-B323),N321+N321-N320)","v":4.5193674160988229},"kW - ligne 3",1514.8919578763255,"de P 15% à P 25%"]
[null,{"$f":"IF(G20=\"UCCLE\",'Fichier météo UCCLE'!$V$8782,'Fichier météo StHubert'!$V$8782)","v":4685},"h    à P > à ",30,"% de Pbesoin",31010,0.11299785008927596,"du temps à P = 35%",5605.8233429289803,"kWh pour la tranche","de 30 à 40 % de P",4242,"h    à P > à ",6.3271143825383529,"kW - ligne 4",3958.9658565025688,"de P 25% à  P 35%"]
[null,{"$f":"IF(G21=\"UCCLE\",'Fichier météo UCCLE'!$U$8782,'Fichier météo StHubert'!$U$8782)","v":3799},"h    à P > à ",40,"% de Pbesoin",43425,0.15823707320628211,"du temps à P = 45%",7850.1412017636558,"kWh pour la tranche","de 40 à 50 % de P",3317,"h    à P > à ",8.134861348977882,"kW - ligne 5",6688.6637758262586,"de P 35% à P 45%"]
[null,{"$f":"IF(G22=\"UCCLE\",'Fichier météo UCCLE'!$T$8782,'Fichier météo StHubert'!$T$8782)","v":2834},"h    à P > à ",50,"% de Pbesoin",61435,0.22386400903691286,"du temps à P = 55%",11105.893488321248,"kWh pour la tranche","de 50 à 60 % de P",2276,"h    à P > à ",9.9426083154174112,"kW - ligne 6",9409.3229603177515,"de P 45% à  P 55%"]
[null,{"$f":"IF(G23=\"UCCLE\",'Fichier météo UCCLE'!$S$8782,'Fichier météo StHubert'!$S$8782)","v":1717},"h    à P > à ",60,"% de Pbesoin",74035,0.26977735670298436,"du temps à P = 65%",13383.654666035054,"kWh pour la tranche","de 60 à 70 % de P",1148,"h    à P > à ",11.75035528185694,"kW - ligne 7",12234.831468862732,"de P 55% à P 65%"]
[null,{"$f":"IF(G24=\"UCCLE\",'Fichier météo UCCLE'!$R$8782,'Fichier météo StHubert'!$R$8782)","v":578},"h    à P > à ",70,"% de Pbesoin",25500,9.2919870276573266E-2,"du temps à P = 75%",4609.7547644207998,"kWh pour la tranche","de 70 à 80 % de P",408,"h    à P > à ",13.558102248296469,"kW - ligne 8",9364.1292861567617,"de P 65 à  P 75%"]
[null,{"$f":"IF(G25=\"UCCLE\",'Fichier météo UCCLE'!$Q$8782,'Fichier météo StHubert'!$Q$8782)","v":238},"h    à P > à ",80,"% de Pbesoin",11220,4.0884742921692238E-2,"du temps à P = 85%",2028.292096345152,"kWh pour la tranche","de 80 à 90 % de P",172,"h    à P > à ",15.365849214736,"kW - ligne 9",3413.0262726378314,"de P 75% à P 85%"]
[null,{"$f":"IF(G26=\"UCCLE\",'Fichier météo UCCLE'!$P$8782,'Fichier météo StHubert'!$P$8782)","v":106},"h    à P > à ",90,"% de Pbesoin",9120,3.3232518310680317E-2,"du temps à P = 95%",1648.6652333928505,"kWh pour la tranche","de 90 à 100 % de P",58,"h    à P > à ",17.173596181175526,"kW - ligne 10",1854.748387566957,"de P 85% à  P 95%"]
[null,{"$f":"IF(G27=\"UCCLE\",'Fichier météo UCCLE'!$O$8782,'Fichier météo StHubert'!$O$8782)","v":10},"h    à P > à ",100,"% de Pbesoin",null,null,null,null,null,null,null,null,null,null,{"$f":"I329/2","v":824.33261669642525},"au-delà de P 95%"]
[null,null,null,null,null,{"$f":"SUM(F320:F329)","v":274430},{"$f":"SUM(G320:G329)","v":0.99999999999999989},null,{"$f":"SUM(I320:I329)","v":49610},"= consommation totale du bâtiment",null,null,null,null,null,{"$f":"SUM(P320:P330)","v":49605.480632583902},"Total en kWh"]
[]
[null,"CADRE 12"]
[null,"Calcul de l'énergie consommée à partir de l'enclenchement de chaque régime de puissance"]
[null,"Numéro de ligne",null,null,"Proportionnelle entre 2 étages de puissance",null,"Besoin pendant",null,"Energie consommée"]
[null,1,null,null,null,null,{"$f":"L320","v":5561},"h",{"$f":"SUM(P320:P330)","v":49605.480632583902},"kWh","Commentaire : = énergie totale consommée"]
[null,{"$f":"MATCH(M296,N$320:N$329,1)","v":{"$error":"#VALUE!"}},null,null,{"$f":"IF(AND(B337<>B336,B337<>10),(INDEX(N$320:N$329,B337+1,1)-M296)/(INDEX(N$320:N$329,B337+1,1)-INDEX(N$320:N$329,B337)),0)","v":{"$error":"#VALUE!"}},null,{"$f":"IF(AND(B337<>B336,B337<>10),(INDEX(L$320:L$329,B337+1,1)+(INDEX(L$320:L$329,B337,1)-INDEX(L$320:L$329,B337+1))*E337),0)","v":{"$error":"#VALUE!"}},"h",{"$f":"IF(AND(B337<>B336,B337<>10),SUM(P$330:INDEX(P$320:P$330,B337+2,1))+INDEX(P$320:P$330,B337+1,1)-((1-E337)*(INDEX(N$320:N$329,B337+1,1)-INDEX(N$320:N$329,B337,1))+2*INDEX(N$320:N$329,B337,1))*(1-E337)/2*(INDEX(L$320:L$329,B337,1)-INDEX(L$320:L$329,B337+1,1)),0)","v":{"$error":"#VALUE!"}},"kWh","Commentaire : = énergie consommée quand puissance demandée est supérieure au 1er étage de puissance"]
[null,{"$error":"#VALUE!"},null,null,{"$error":"#VALUE!"},null,{"$error":"#VALUE!"},"h",{"$f":"IF(AND(B338<>B337,B338<>10),SUM(P$330:INDEX(P$320:P$330,B338+2,1))+INDEX(P$320:P$330,B338+1,1)-((1-E338)*(INDEX(N$320:N$329,B338+1,1)-INDEX(N$320:N$329,B338,1))+2*INDEX(N$320:N$329,B338,1))*(1-E338)/2*(INDEX(L$320:L$329,B338,1)-INDEX(L$320:L$329,B338+1,1)),0)","v":{"$error":"#VALUE!"}},"kWh","Commentaire : = énergie consommée quand puissance demandée est supérieure au 2ème étage de puissance"]
[null,{"$error":"#VALUE!"},null,null,{"$error":"#VALUE!"},null,{"$error":"#VALUE!"},"h",{"$f":"IF(AND(B339<>B338,B339<>10),SUM(P$330:INDEX(P$320:P$330,B339+2,1))+INDEX(P$320:P$330,B339+1,1)-((1-E339)*(INDEX(N$320:N$329,B339+1,1)-INDEX(N$320:N$329,B339,1))+2*INDEX(N$320:N$329,B339,1))*(1-E339)/2*(INDEX(L$320:L$329,B339,1)-INDEX(L$320:L$329,B339+1,1)),0)","v":{"$error":"#VALUE!"}},"kWh","Commentaire : = énergie consommée quand puissance demandée est supérieure au 3ème étage de puissance"]
[null,{"$error":"#VALUE!"},null,null,{"$error":"#VALUE!"},null,{"$error":"#VALUE!"},"h",{"$f":"IF(AND(B340<>B339,B340<>10),SUM(P$330:INDEX(P$320:P$330,B340+2,1))+INDEX(P$320:P$330,B340+1,1)-((1-E340)*(INDEX(N$320:N$329,B340+1,1)-INDEX(N$320:N$329,B340,1))+2*INDEX(N$320:N$329,B340,1))*(1-E340)/2*(INDEX(L$320:L$329,B340,1)-INDEX(L$320:L$329,B340+1,1)),0)","v":{"$error":"#VALUE!"}},"kWh","Commentaire : = énergie consommée quand puissance demandée est supérieure au 4ème étage de puissance"]
[null,{"$error":"#VALUE!"},null,null,{"$error":"#VALUE!"},null,{"$error":"#VALUE!"},"h",{"$f":"IF(AND(B341<>B340,B341<>10),SUM(P$330:INDEX(P$320:P$330,B341+2,1))+INDEX(P$320:P$330,B341+1,1)-((1-E341)*(INDEX(N$320:N$329,B341+1,1)-INDEX(N$320:N$329,B341,1))+2*INDEX(N$320:N$329,B341,1))*(1-E341)/2*(INDEX(L$320:L$329,B341,1)-INDEX(L$320:L$329,B341+1,1)),0)","v":{"$error":"#VALUE!"}},"kWh","Commentaire : = énergie consommée quand puissance demandée est supérieure au 5ème étage de puissance"]
[null,{"$error":"#VALUE!"},null,null,{"$error":"#VALUE!"},null,{"$error":"#VALUE!"},"h",{"$f":"IF(AND(B342<>B341,B342<>10),SUM(P$330:INDEX(P$320:P$330,B342+2,1))+INDEX(P$320:P$330,B342+1,1)-((1-E342)*(INDEX(N$320:N$329,B342+1,1)-INDEX(N$320:N$329,B342,1))+2*INDEX(N$320:N$329,B342,1))*(1-E342)/2*(INDEX(L$320:L$329,B342,1)-INDEX(L$320:L$329,B342+1,1)),0)","v":{"$error":"#VALUE!"}},"kWh","Commentaire : = énergie consommée quand puissance demandée est supérieure au 6ème étage de puissance"]
[null,{"$error":"#VALUE!"},null,null,{"$error":"#VALUE!"},null,{"$error":"#VALUE!"},"h",{"$f":"IF(AND(B343<>B342,B343<>10),SUM(P$330:INDEX(P$320:P$330,B343+2,1))+INDEX(P$320:P$330,B343+1,1)-((1-E343)*(INDEX(N$320:N$329,B343+1,1)-INDEX(N$320:N$329,B343,1))+2*INDEX(N$320:N$329,B343,1))*(1-E343)/2*(INDEX(L$320:L$329,B343,1)-INDEX(L$320:L$329,B343+1,1)),0)","v":{"$error":"#VALUE!"}},"kWh","Commentaire : = énergie consommée quand puissance demandée est supérieure au 7ème étage de puissance"]
[null,{"$error":"#VALUE!"},null,null,{"$error":"#VALUE!"},null,{"$error":"#VALUE!"},"h",{"$f":"IF(AND(B344<>B343,B344<>10),SUM(P$330:INDEX(P$320:P$330,B344+2,1))+INDEX(P$320:P$330,B344+1,1)-((1-E344)*(INDEX(N$320:N$329,B344+1,1)-INDEX(N$320:N$329,B344,1))+2*INDEX(N$320:N$329,B344,1))*(1-E344)/2*(INDEX(L$320:L$329,B344,1)-INDEX(L$320:L$329,B344+1,1)),0)","v":{"$error":"#VALUE!"}},"kWh","Commentaire : = énergie consommée quand puissance demandée est supérieure au 8ème étage de puissance"]
[]
[null,"CADRE 13"]
[null,"kWh/an = consommation pour chaque tranche de puissance"]
[null,null,"Comb1","Comb2","Comb3","Comb4","Comb5","Comb6","Comb7","Comb8"]
[null,{"$f":"IF(Données!$B$33=1,INDEX('Calcul du rendement'!C308:J308,1,Données!$B$27),INDEX('Calcul du rendement'!C308:J308,1,'Calcul du rendement'!F264))","v":"- Chaudière 1"},{"$f":"ROUND(I336,0)","v":49605},{"$f":"ROUND(I336-D350,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I336-E350,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I336-F350-F351-F352,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I336-G350-G351,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I336-H354-H353-H352-H351-H350,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I336-I350-I351-I352,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I336-J350-J351-J352-J353-J354-J355-J356,0)","v":{"$error":"#VALUE!"}}]
[null,{"$f":"IF(Données!$B$33=1,INDEX('Calcul du rendement'!C309:J309,1,Données!$B$27),INDEX('Calcul du rendement'!C309:J309,1,'Calcul du rendement'!F264))","v":"- -"},0,{"$f":"ROUND(I337,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I337-M296*G337,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I337-F351-F352,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I337-G351-M296*G337,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I337-H351-H352-H353-H354,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I337-I352-I351-G337*M296,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I337-J351-J352-J353-J354-J355-J356,0)","v":{"$error":"#VALUE!"}},null,"Commentaire : = énergie à produire lorsque la puissance demandée dépasse la puissance"]
[null,{"$f":"IF(Données!$B$33=1,INDEX('Calcul du rendement'!C310:J310,1,Données!$B$27),INDEX('Calcul du rendement'!C310:J310,1,'Calcul du rendement'!F264))","v":"- -"},0,0,0,{"$f":"ROUND(I338-F352-M297*(G338-G339),0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I338-M297*G338,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I338-H352-H353-H354-M297*G338,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I338-I352-G338*M297,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I338-J352-J353-J354-J355-J356-M297*G338,0)","v":{"$error":"#VALUE!"}},null,null,"de la 1ere allure moins ce que produit la 1ere allure pendant cette période = "]
[null,{"$f":"IF(Données!$B$33=1,INDEX('Calcul du rendement'!C311:J311,1,Données!$B$27),INDEX('Calcul du rendement'!C311:J311,1,'Calcul du rendement'!F264))","v":"- -"},0,0,0,{"$f":"ROUND(I339-M297*G339,0)","v":{"$error":"#VALUE!"}},0,{"$f":"ROUND(I339-H353-H354-E193*G339,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I339-G339*M298,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I339-J353-J354-J355-J356-M297*G339,0)","v":{"$error":"#VALUE!"}},null,null,"ce que produit la 2eme allure"]
[null,{"$f":"IF(Données!$B$33=1,INDEX('Calcul du rendement'!C312:J312,1,Données!$B$27),INDEX('Calcul du rendement'!C312:J312,1,'Calcul du rendement'!F264))","v":"- -"},0,0,0,0,0,{"$f":"ROUND(I340-H354-G340*M299,0)","v":{"$error":"#VALUE!"}},0,{"$f":"ROUND(I340-J354-J355-J356-M299*G340,0)","v":{"$error":"#VALUE!"}},null,null,"Attention, ce calcul tient compte de l'ordre d'enclenchement de la cascade."]
[null,{"$f":"IF(Données!$B$33=1,INDEX('Calcul du rendement'!C313:J313,1,Données!$B$27),INDEX('Calcul du rendement'!C313:J313,1,'Calcul du rendement'!F264))","v":"- -"},0,0,0,0,0,{"$f":"ROUND(I341-M299*G341,0)","v":{"$error":"#VALUE!"}},0,{"$f":"ROUND(I341-J355-J356-M299*G341,0)","v":{"$error":"#VALUE!"}},null,null,"Par exemple, quand la deuxième allure est enclenchée, la première allure"]
[null,{"$f":"IF(Données!$B$33=1,INDEX('Calcul du rendement'!C314:J314,1,Données!$B$27),INDEX('Calcul du rendement'!C314:J314,1,'Calcul du rendement'!F264))","v":"- -"},0,0,0,0,0,0,0,{"$f":"ROUND(I342-J356-M301*G342,0)","v":{"$error":"#VALUE!"}},null,null,"du brûleur disparaît."]
[null,{"$f":"IF(Données!$B$33=1,INDEX('Calcul du rendement'!C315:J315,1,Données!$B$27),INDEX('Calcul du rendement'!C315:J315,1,'Calcul du rendement'!F264))","v":"- -"},0,0,0,0,0,0,0,{"$f":"ROUND(I343-M301*G343,0)","v":{"$error":"#VALUE!"}}]
[null,null,{"$f":"SUM(C349:C356)","v":49605},{"$f":"SUM(D349:D356)","v":{"$error":"#VALUE!"}},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[]
[null,"CADRE 14"]
[null,"heures/an = consommation / puissance du brûleur à  chaque allure = heures de fonctionnement de chaque allure des chaudières"]
[null,null,"Comb1","Comb2","Comb3","Comb4","Comb5","Comb6","Comb7","Comb8"]
[null,{"$f":"B349","v":"- Chaudière 1"},{"$f":"ROUND(C349/E192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(D349/E192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(E349/E192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(F349/E192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(G349/E192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(H349/E192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I349/E192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(J349/E192,0)","v":{"$error":"#VALUE!"}}]
[null,"- -",0,{"$f":"ROUND(D350/E193,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(E350/F192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(F350/E193,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(G350/F192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(H350/E193,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I350/F192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(J350/E193,0)","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,{"$f":"ROUND(F351/F192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(G351/G192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(H351/F192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I351/G192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(J351/F192,0)","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,{"$f":"ROUND(F352/F193,0)","v":{"$error":"#VALUE!"}},0,{"$f":"ROUND(H352/F193,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(I352/H192,0)","v":{"$error":"#VALUE!"}},{"$f":"ROUND(J352/F193,0)","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,0,0,{"$f":"ROUND(H353/G192,0)","v":{"$error":"#VALUE!"}},0,{"$f":"ROUND(J353/G192,0)","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,0,0,{"$f":"ROUND(H354/G193,0)","v":{"$error":"#VALUE!"}},0,{"$f":"ROUND(J354/G193,0)","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,0,0,0,0,{"$f":"ROUND(J355/H192,0)","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,0,0,0,0,{"$f":"ROUND(J356/H193,0)","v":{"$error":"#VALUE!"}}]
[]
[null,"CADRE 15"]
[null,"heures/an quand la puissance de chaque chaudière est nécessaire"]
[null,null,"Comb1","Comb2","Comb3","Comb4","Comb5","Comb6","Comb7","Comb8"]
[null,{"$f":"B349","v":"- Chaudière 1"},{"$f":"'Calcul du rendement'!E59","v":5808},{"$f":"C374","v":5808},{"$f":"D374","v":5808},{"$f":"E374","v":5808},{"$f":"E374","v":5808},{"$f":"G374","v":5808},{"$f":"H374","v":5808},{"$f":"I374","v":5808}]
[null,"- -",0,{"$f":"D374","v":5808},{"$f":"G337","v":{"$error":"#VALUE!"}},{"$f":"ROUND(F374,0)","v":5808},{"$f":"G337","v":{"$error":"#VALUE!"}},{"$f":"ROUND(H374,0)","v":5808},{"$f":"G337","v":{"$error":"#VALUE!"}},{"$f":"ROUND(J374,0)","v":5808}]
[null,"- -",0,0,0,{"$f":"ROUND(G338,0)","v":{"$error":"#VALUE!"}},{"$f":"G338","v":{"$error":"#VALUE!"}},{"$f":"ROUND(G338,0)","v":{"$error":"#VALUE!"}},{"$f":"G338","v":{"$error":"#VALUE!"}},{"$f":"ROUND(G338,0)","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,{"$f":"ROUND(F376,0)","v":{"$error":"#VALUE!"}},0,{"$f":"ROUND(H376,0)","v":{"$error":"#VALUE!"}},{"$f":"G339","v":{"$error":"#VALUE!"}},{"$f":"ROUND(J376,0)","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,0,0,{"$f":"ROUND(G340,0)","v":{"$error":"#VALUE!"}},0,{"$f":"ROUND(G340,0)","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,0,0,{"$f":"ROUND(H378,0)","v":{"$error":"#VALUE!"}},0,{"$f":"ROUND(J378,0)","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,0,0,0,0,{"$f":"ROUND(G342,0)","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,0,0,0,0,{"$f":"ROUND(J380,0)","v":{"$error":"#VALUE!"}}]
[]
[null,"CADRE 16"]
[null,"Durée de fonctionnement de la chaudière (nT)"]
[null,null,"Comb1","Comb2","Comb3","Comb4","Comb5","Comb6","Comb7","Comb8"]
[null,{"$f":"B349","v":"- Chaudière 1"},{"$f":"C374","v":5808},0,{"$f":"E374","v":5808},0,{"$f":"G374","v":5808},0,{"$f":"I374","v":5808},0]
[null,{"$f":"B350","v":"- -"},0,{"$f":"D375","v":5808},{"$error":"#VALUE!"},5808,{"$error":"#VALUE!"},5808,{"$error":"#VALUE!"},5808]
[null,{"$f":"B351","v":"- -"},0,0,0,0,{"$f":"G376","v":{"$error":"#VALUE!"}},0,{"$f":"I376","v":{"$error":"#VALUE!"}},0]
[null,"- -",0,0,0,{"$f":"F377","v":{"$error":"#VALUE!"}},0,{"$f":"H377","v":{"$error":"#VALUE!"}},{"$f":"I377","v":{"$error":"#VALUE!"}},{"$f":"J377","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,0,0,0,0,0]
[null,"- -",0,0,0,0,0,{"$f":"H379","v":{"$error":"#VALUE!"}},0,{"$f":"J379","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,0,0,0,0,0]
[null,"- -",0,0,0,0,0,0,0,{"$f":"J381","v":{"$error":"#VALUE!"}}]
[]
[null,"CADRE 17"]
[null,"Durée de fonctionnement du brûleur (nFT)"]
[null,null,"Comb1","Comb2","Comb3","Comb4","Comb5","Comb6","Comb7","Comb8"]
[null,{"$f":"B349","v":"- Chaudière 1"},{"$f":"H199","v":{"$error":"#VALUE!"}},0,{"$f":"H199","v":{"$error":"#VALUE!"}},0,{"$f":"H199","v":{"$error":"#VALUE!"}},0,{"$f":"H199","v":{"$error":"#VALUE!"}},0]
[null,{"$f":"B350","v":"- -"},0,{"$f":"H199+H200","v":{"$error":"#VALUE!"}},{"$f":"H200","v":""},{"$f":"H199+H200","v":{"$error":"#VALUE!"}},{"$f":"H200","v":""},{"$f":"H199+H200","v":{"$error":"#VALUE!"}},{"$f":"H200","v":""},{"$f":"H199+H200","v":{"$error":"#VALUE!"}}]
[null,{"$f":"B351","v":"- -"},0,0,0,0,{"$f":"H201","v":""},0,{"$f":"H201","v":""},0]
[null,"- -",0,0,0,{"$f":"H201+H202","v":{"$error":"#VALUE!"}},0,{"$f":"H201+H202","v":{"$error":"#VALUE!"}},{"$f":"H202","v":""},{"$f":"H201+H202","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,0,0,0,0,0]
[null,"- -",0,0,0,0,0,{"$f":"H203+H204","v":{"$error":"#VALUE!"}},0,{"$f":"H203+H204","v":{"$error":"#VALUE!"}}]
[null,"- -",0,0,0,0,0,0,0,0]
[null,"- -",0,0,0,0,0,0,0,{"$f":"H205+H206","v":{"$error":"#VALUE!"}}]
[]
[null,"CADRE 18"]
[null,"Rendement utile (rendement de combustion - pertes vers l'ambiance) pour chacun des étages de puissance"]
[null,null,"Comb1","Comb2","Comb3","Comb4","Comb5","Comb6","Comb7","Comb8"]
[null,{"$f":"B349","v":"- Chaudière 1"},{"$f":"IF(Données!$B$33=1,(IF($G180=\"-\",0,$G180)+IF($H180=\"-\",0,$H180)+IF($I180=\"-\",0,$I180)+IF($J180=\"-\",0,$J180))/$E$64,G180)","v":{"$error":"#VALUE!"}},{"$f":"C410","v":{"$error":"#VALUE!"}},{"$f":"G180","v":{"$error":"#VALUE!"}},{"$f":"G180","v":{"$error":"#VALUE!"}},{"$f":"G180","v":{"$error":"#VALUE!"}},{"$f":"G180","v":{"$error":"#VALUE!"}},{"$f":"G180","v":{"$error":"#VALUE!"}},{"$f":"G180","v":{"$error":"#VALUE!"}}]
[null,{"$f":"B350","v":"- -"},0,{"$f":"IF(Données!$B$33=1,(IF($G181=\"-\",0,$G181)+IF($H181=\"-\",0,$H181)+IF($I181=\"-\",0,$I181)+IF($J181=\"-\",0,$J181))/$E$64,G181)","v":"-"},{"$f":"H180","v":"-"},{"$f":"G181","v":"-"},{"$f":"H180","v":"-"},{"$f":"G181","v":"-"},{"$f":"H180","v":"-"},{"$f":"G181","v":"-"}]
[null,{"$f":"B351","v":"- -"},0,0,0,{"$f":"H180","v":"-"},{"$f":"I180","v":"-"},{"$f":"H180","v":"-"},{"$f":"I180","v":"-"},{"$f":"H180","v":"-"}]
[null,"- -",0,0,0,{"$f":"H181","v":"-"},0,{"$f":"H181","v":"-"},{"$f":"J180","v":"-"},{"$f":"H181","v":"-"}]
[null,"- -",0,0,0,0,0,{"$f":"I180","v":"-"},0,{"$f":"I180","v":"-"}]
[null,"- -",0,0,0,0,0,{"$f":"I181","v":"-"},0,{"$f":"I181","v":"-"}]
[null,"- -",0,0,0,0,0,0,0,{"$f":"J180","v":"-"}]
[null,"- -",0,0,0,0,0,0,0,{"$f":"J181","v":"-"}]
[]
[null,"CADRE 19"]
[null,null,"Rend utile","Cons","Perte comb","Pn","qE","nT","nT *","nFT","nT-nFT","nT-nFT *","qE x Pn x (nT-nFT)","qE x Pn x (nT-nFT) *",null,"nT = durée de fonctionnement de la chaudière"]
[null,{"$f":"B349","v":"- Chaudière 1"},{"$f":"IF(Données!$B$33=1,INDEX(C410:R410,1,2*Données!$B$27),INDEX(C410:R410,1,'Calcul du rendement'!F264))","v":{"$error":"#VALUE!"}},{"$f":"IF(INDEX(C349:J349,1,'Calcul du rendement'!F264)<0,0,INDEX(C349:J349,1,'Calcul du rendement'!F264))","v":49605},{"$f":"IF(C421=\"-\",0,D421*(1-C421/100))","v":{"$error":"#VALUE!"}},{"$f":"IF(P82=1,M284,0)","v":{"$error":"#VALUE!"}},{"$f":"IF(P82=1,G182,G182)","v":"-"},{"$f":"IF(Données!$B$33=1,INDEX(C386:J386,1,Données!$B$27),INDEX(C386:J386,1,F264))","v":5808},{"$f":"'Calcul du rendement'!E59","v":5808},{"$f":"IF(Données!$B$33=1,INDEX(C398:J398,1,Données!$B$27),INDEX(C398:J398,1,'Calcul du rendement'!F264))","v":{"$error":"#VALUE!"}},{"$f":"H421-J421","v":{"$error":"#VALUE!"}},{"$f":"I421-J421","v":{"$error":"#VALUE!"}},{"$f":"G421/100*F421*K421","v":{"$error":"#VALUE!"}},{"$f":"G421/100*F421*L421","v":{"$error":"#VALUE!"}},null,"nFT = durée de fonctionnement du brûleur"]
[null,{"$f":"B350","v":"- -"},{"$f":"IF(Données!$B$33=1,INDEX(C411:R411,1,2*Données!$B$27),INDEX(C411:R411,1,'Calcul du rendement'!F264))","v":0},{"$f":"IF(INDEX(C350:J350,1,'Calcul du rendement'!F264)<0,0,INDEX(C350:J350,1,'Calcul du rendement'!F264))","v":0},{"$f":"IF(C422=\"-\",0,D422*(1-C422/100))","v":0},{"$f":"IF(P82=1,M285,M285)","v":0},{"$f":"IF(P82=1,H182,G182)","v":"-"},{"$f":"IF(Données!$B$33=1,INDEX(C387:J387,1,Données!$B$27),INDEX(C387:J387,1,'Calcul du rendement'!F264))","v":0},{"$f":"I421","v":5808},{"$f":"IF(Données!$B$33=1,INDEX(C399:J399,1,Données!$B$27),INDEX(C399:J399,1,'Calcul du rendement'!F264))","v":0},0,5808,{"$f":"IF(G422=\"-\",0,G422/100*F422*K422)","v":0},{"$f":"IF(G422=\"-\",0,G422/100*F422*L422)","v":0},null,"qE = pertes à l'arrêt"]
[null,{"$f":"B351","v":"- -"},{"$f":"IF(Données!$B$33=1,INDEX(C412:R412,1,2*Données!$B$27),INDEX(C412:R412,1,'Calcul du rendement'!F264))","v":0},{"$f":"IF(INDEX(C351:J351,1,'Calcul du rendement'!F264)<0,0,INDEX(C351:J351,1,'Calcul du rendement'!F264))","v":0},0,{"$f":"IF(P82=1,M286,0)","v":0},{"$f":"IF(P82=1,I182,H182)","v":"-"},{"$f":"IF(Données!$B$33=1,INDEX(C388:J388,1,Données!$B$27),INDEX(C388:J388,1,'Calcul du rendement'!F264))","v":0},5808,{"$f":"IF(Données!$B$33=1,INDEX(C400:J400,1,Données!$B$27),INDEX(C400:J400,1,'Calcul du rendement'!F264))","v":0},0,5808,0,{"$f":"IF(G423=\"-\",0,G423/100*F423*L423)","v":0},null,"Pn = puissance nominale"]
[null,"- -",{"$f":"IF(Données!$B$33=1,INDEX(C413:R413,1,2*Données!$B$27),INDEX(C413:R413,1,'Calcul du rendement'!F264))","v":0},{"$f":"IF(INDEX(C352:J352,1,'Calcul du rendement'!F264)<0,0,INDEX(C352:J352,1,'Calcul du rendement'!F264))","v":0},0,{"$f":"IF(P82=1,M287,M287)","v":0},{"$f":"IF(P82=1,J182,H182)","v":"-"},{"$f":"IF(Données!$B$33=1,INDEX(C389:J389,1,Données!$B$27),INDEX(C389:J389,1,'Calcul du rendement'!F264))","v":0},5808,{"$f":"IF(Données!$B$33=1,INDEX(C401:J401,1,Données!$B$27),INDEX(C401:J401,1,'Calcul du rendement'!F264))","v":0},0,5808,0,0,null,"* si les chaudières ne sont pas isolées hydrauliquement"]
[null,"- -",{"$f":"IF(Données!$B$33=1,INDEX(C414:R414,1,2*Données!$B$27),INDEX(C414:R414,1,'Calcul du rendement'!F264))","v":0},{"$f":"IF(INDEX(C353:J353,1,'Calcul du rendement'!F264)<0,0,INDEX(C353:J353,1,'Calcul du rendement'!F264))","v":0},0,0,{"$f":"IF(P82=1,\"-\",I182)","v":"-"},{"$f":"IF(Données!$B$33=1,INDEX(C390:J390,1,Données!$B$27),INDEX(C390:J390,1,'Calcul du rendement'!F264))","v":0},5808,{"$f":"IF(Données!$B$33=1,INDEX(C402:J402,1,Données!$B$27),INDEX(C402:J402,1,'Calcul du rendement'!F264))","v":0},0,5808,0,0]
[null,"- -",{"$f":"IF(Données!$B$33=1,INDEX(C415:R415,1,2*Données!$B$27),INDEX(C415:R415,1,'Calcul du rendement'!F264))","v":0},{"$f":"IF(INDEX(C354:J354,1,'Calcul du rendement'!F264)<0,0,INDEX(C354:J354,1,'Calcul du rendement'!F264))","v":0},0,{"$f":"IF(P82=1,0,M289)","v":0},{"$f":"IF(P82=1,\"-\",I182)","v":"-"},{"$f":"IF(Données!$B$33=1,INDEX(C391:J391,1,Données!$B$27),INDEX(C391:J391,1,'Calcul du rendement'!F264))","v":0},5808,{"$f":"IF(Données!$B$33=1,INDEX(C403:J403,1,Données!$B$27),INDEX(C403:J403,1,'Calcul du rendement'!F264))","v":0},0,5808,0,0]
[null,"- -",{"$f":"IF(Données!$B$33=1,INDEX(C416:R416,1,2*Données!$B$27),INDEX(C416:R416,1,'Calcul du rendement'!F264))","v":0},{"$f":"IF(INDEX(C355:J355,1,'Calcul du rendement'!F264)<0,0,INDEX(C355:J355,1,'Calcul du rendement'!F264))","v":0},0,0,{"$f":"IF(P82=1,\"-\",J182)","v":"-"},{"$f":"IF(Données!$B$33=1,INDEX(C392:J392,1,Données!$B$27),INDEX(C392:J392,1,'Calcul du rendement'!F264))","v":0},5808,{"$f":"IF(Données!$B$33=1,INDEX(C404:J404,1,Données!$B$27),INDEX(C404:J404,1,'Calcul du rendement'!F264))","v":0},0,5808,0,0]
[null,"- -",{"$f":"IF(Données!$B$33=1,INDEX(C417:R417,1,2*Données!$B$27),INDEX(C417:R417,1,'Calcul du rendement'!F264))","v":0},{"$f":"IF(INDEX(C356:J356,1,'Calcul du rendement'!F264)<0,0,INDEX(C356:J356,1,'Calcul du rendement'!F264))","v":0},0,{"$f":"IF(P82=1,0,M291)","v":0},{"$f":"IF(P82=1,\"-\",J182)","v":"-"},{"$f":"IF(Données!$B$33=1,INDEX(C393:J393,1,Données!$B$27),INDEX(C393:J393,1,'Calcul du rendement'!F264))","v":0},5808,{"$f":"IF(Données!$B$33=1,INDEX(C405:J405,1,Données!$B$27),INDEX(C405:J405,1,'Calcul du rendement'!F264))","v":0},0,5808,0,0]
[null,null,null,{"$f":"SUM(D421:D428)","v":49605},{"$f":"SUM(E421:E428)","v":{"$error":"#VALUE!"}},null,null,null,null,null,null,null,{"$f":"SUM(M421:M428)","v":{"$error":"#VALUE!"}},{"$f":"SUM(N421:N428)","v":{"$error":"#VALUE!"}},"TOT"]

{"sheet":"T° retour condensation","index":2,"n_rows":13,"n_cols":3,"rows_kept":13,"cut":false,"hidden":false,"merged":[]}
[]
[null,"Evaluation de la température moyenne de retour pour les chaudières à condensation"]
[]
[]
[null,"Questions d'évaluation"]
[]
[null,"By Pass (bouclage collecteur ou bouteille casse-pression ou présence circuits secondaires équipés de vanne 3 voies diviseuse)"]
[]
[null,"Régulation de la ou des chaudières en température glissante"]
[]
[null,"Régulation des circuits secondaires en température glissante"]
[]
[null,"Température de retour moyenne en °C",{"$f":"+VLOOKUP(Données!I72,Données!D57:E74,2)","v":"Inférieure à 45°C"}]

{"sheet":"Fichier météo UCCLE","index":3,"n_rows":8783,"n_cols":25,"rows_kept":2250,"cut":true,"hidden":true,"merged":[[17,11,18,11],[17,1,18,1],[17,2,18,2],[17,3,18,3],[17,4,18,4],[17,8,18,8]],"bounds":{"rows_first":1000,"rows_last":250,"rows_between":1000,"halvings":1}}
[]
[null,"Etablissement de la monotone de chaleur"]
[]
[null,"T° cons jour =",{"$f":"'Calcul du rendement'!F42","v":19},"°C","Gain de température pour apports gratuits :",null,null,null,null,{"$f":"'Calcul du rendement'!F44","v":2},"°C","Température extérieure moyenne sur l'année",null,null,null,null,null,{"$f":"SUM(I22:I8781)/8760","v":9.8844863013698596},"°C"]
[null,"T° cons nuit =",{"$f":"'Calcul du rendement'!F43","v":16},"°C","Température de jour effective :",null,null,null,null,{"$f":"C4-J4","v":17},"°C","Température extérieure moyenne saison de chauffe",null,null,null,null,null,{"$f":"(SUM(I22:I3237)+SUM(I6190:I8781))/5800","v":7.0037068965517388},"°C","soit du 15 septembre au 15 mai"]
[null,null,null,null,null,null,null,null,null,null,null,"Température extérieure moyenne hors saison de chauffe",null,null,null,null,null,{"$f":"SUM(I3238:I6190)/2960","v":15.534763513513496},"°C","soit du 15 mai au 15 septembre"]
[null,null,"Plage 1","Plage 2"]
[null,null,true,false]
[null,"Heure début",{"$f":"IF($C$8,'Calcul du rendement'!F36,0)","v":8},{"$f":"IF($D$8,'Calcul du rendement'!$F$37,0)","v":0},"h",null,"Horaire hebdomadaire :",null,1]
[null,"Heure fin",{"$f":"IF($C$8,'Calcul du rendement'!H36,0)","v":18},{"$f":"IF($D$8,'Calcul du rendement'!H37,0)","v":0},"h"]
[]
[null,"Jour arrêt chauffage",null,{"$f":"'Calcul du rendement'!E50","v":15},null,null,"Jour début chauffage",null,{"$f":"'Calcul du rendement'!E51","v":15}]
[null,"Mois arrêt chauffage",null,{"$f":"'Calcul du rendement'!F50","v":5},null,null,"Mois début chauffage",null,{"$f":"'Calcul du rendement'!F51","v":9}]
[]
[]
[null,"T° de base",{"$f":"'Calcul du rendement'!G20","v":-8},"°C"]
[]
[null,"Mois","Semaine","Jour","Heure","Saison","Horaire","Horaire","T° ext. ",null,null,"T° int."]
[null,null,null,null,null,"chauffe","école","hebdomadaire",null,null,null,null,null,null,null,null,null,null,null,"Monotone de chaleur"]
[null,null,null,null,null,{"$f":"SUM(F22:F8781)","v":5808},null,null,null,null,null,null,null,"Formule :","= 1 x Saison de chauffe si (Tint - Text) / (Tconsigne - Tbase) > %Puissance"]
[null,null,null,null,null,"[h]",null,null,"[°C]",null,null,"[°C]",null,"% Puissance",1,{"$f":"0.9","v":0.9},0.8,0.7,0.6,0.5,0.4,0.3,0.2,0.1,0]
[null,1,1,1,1,{"$f":"IF(AND(B22>$D$13,B22<$I$13),0,IF(B22=$D$13,IF(D22>=$D$12,0,1),IF(B22=$I$13,IF(D22<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C22=7),AND($I$9=1,C22>5)),\"n\",IF($I$9=2,G22,\"j\"))","v":"j"},7,null,null,{"$f":"IF(AND(H22=\"j\",OR(AND($C$9<=E22,E22<$C$10),AND($D$9<=E22,E22<$D$10))),$J$5,$C$5)*F22","v":16},null,null,{"$f":"IF(($L22-$I22)/(($C$4-$C$16))>=O$21,1*$F22,0)","v":0},{"$f":"IF(($L22-$I22)/(($C$4-$C$16))>=P$21,1*$F22,0)","v":0},0,0,0,0,0,1,1,1,1]
[null,1,1,1,2,{"$f":"IF(AND(B23>$D$13,B23<$I$13),0,IF(B23=$D$13,IF(D23>=$D$12,0,1),IF(B23=$I$13,IF(D23<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C23=7),AND($I$9=1,C23>5)),\"n\",IF($I$9=2,G23,\"j\"))","v":"j"},6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,1,1,3,1,"n",{"$f":"IF(OR(AND($I$9=3,C24=7),AND($I$9=1,C24>5)),\"n\",IF($I$9=2,G24,\"j\"))","v":"j"},5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,1,1,4,1,"n",{"$f":"IF(OR(AND($I$9=3,C25=7),AND($I$9=1,C25>5)),\"n\",IF($I$9=2,G25,\"j\"))","v":"j"},5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,1,1,5,1,"n",{"$f":"IF(OR(AND($I$9=3,C26=7),AND($I$9=1,C26>5)),\"n\",IF($I$9=2,G26,\"j\"))","v":"j"},5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,6,1,"n","j",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,7,1,"n","j",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,8,1,"n",{"$f":"IF(OR(AND($I$9=3,C29=7),AND($I$9=1,C29>5)),\"n\",IF($I$9=2,G29,\"j\"))","v":"j"},4.0999999999999996,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,9,1,"n","j",4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,10,1,"n","j",4.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,11,1,"n","j",4.7,null,null,17,null,null,{"$f":"IF(($L32-$I32)/(($C$4-$C$16))>=O$21,1*$F32,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,12,1,"n","j",5.4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,13,1,"n","j",6.1,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,14,1,"n","j",6.3,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,1,1,15,1,"n","j",6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,16,1,"n","j",6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,17,1,"n","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,18,1,"n","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,1,1,19,1,"n","j",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,20,1,"n","j",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,21,1,"n","j",4.5,null,null,16,null,null,{"$f":"IF(($L42-$I42)/(($C$4-$C$16))>=O$21,1*$F42,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,22,1,"n","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,23,1,"n","j",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,1,24,1,"n","j",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,2,1,1,"n","j",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,2,2,1,"n","j",2.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,3,1,"n","j",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,4,1,"n","j",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,5,1,"n","j",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,6,1,"n","j",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,7,1,"n","j",1.6,null,null,16,null,null,{"$f":"IF(($L52-$I52)/(($C$4-$C$16))>=O$21,1*$F52,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,8,1,"n","j",1.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,9,1,"n","j",1.1000000000000001,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,10,1,"n","j",1.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,11,1,"n","j",1.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,12,1,"n","j",2.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,13,1,"n","j",3.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,2,14,1,"n","j",4.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,2,15,1,"n","j",4.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,2,16,1,"n","j",4.0999999999999996,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,2,17,1,"n","j",3.7,null,null,17,null,null,{"$f":"IF(($L62-$I62)/(($C$4-$C$16))>=O$21,1*$F62,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,2,2,18,1,"n","j",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,2,19,1,"n","j",2.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,20,1,"n","j",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,21,1,"n","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,22,1,"n","j",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,23,1,"n","j",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,2,24,1,"n","j",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,1,1,"n","j",2.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,3,2,1,"n","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,3,3,1,"n","j",2.8,null,null,16,null,null,{"$f":"IF(($L72-$I72)/(($C$4-$C$16))>=O$21,1*$F72,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,3,3,4,1,"n","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,3,5,1,"n","j",2.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,6,1,"n","j",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,7,1,"n","j",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,8,1,"n","j",1.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,9,1,"n","j",1.6,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,10,1,"n","j",1.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,11,1,"n","j",1.6,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,12,1,"n","j",2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,13,1,"n","j",1.6,null,null,17,null,null,{"$f":"IF(($L82-$I82)/(($C$4-$C$16))>=O$21,1*$F82,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,14,1,"n","j",1.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,15,1,"n","j",2.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,16,1,"n","j",3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,17,1,"n","j",3,null,null,{"$f":"IF(AND(H86=\"j\",OR(AND($C$9<=E86,E86<$C$10),AND($D$9<=E86,E86<$D$10))),$J$5,$C$5)*F86","v":17},null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,3,18,{"$f":"IF(AND(B87>$D$13,B87<$I$13),0,IF(B87=$D$13,IF(D87>=$D$12,0,1),IF(B87=$I$13,IF(D87<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C87=7),AND($I$9=1,C87>5)),\"n\",IF($I$9=2,G87,\"j\"))","v":"j"},3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,3,19,1,"n","j",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,3,20,1,"n","j",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,3,21,1,"n","j",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,3,22,1,"n","j",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,3,23,1,"n","j",3.1,null,null,16,null,null,{"$f":"IF(($L92-$I92)/(($C$4-$C$16))>=O$21,1*$F92,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,3,3,24,1,"n","j",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,4,1,1,"n","j",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,4,2,1,"n","j",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,4,3,1,"n","j",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,4,4,1,"n","j",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,4,5,1,"n","j",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,4,6,1,"n","j",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,4,7,1,"n","j",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,4,8,1,"n","j",2.2000000000000002,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,9,1,"n","j",1.6,null,null,17,null,null,{"$f":"IF(($L102-$I102)/(($C$4-$C$16))>=O$21,1*$F102,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,10,1,"n","j",1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,11,1,"n","j",1.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,12,1,"n","j",2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,13,1,"n","j",2.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,14,1,"n","j",2.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,15,1,"n","j",2.2999999999999998,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,16,1,"n","j",2.1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,17,1,"n","j",1.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,18,1,"n","j",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,19,1,"n","j",1.4,null,null,16,null,null,{"$f":"IF(($L112-$I112)/(($C$4-$C$16))>=O$21,1*$F112,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,20,1,"n","j",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,21,1,"n","j",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,22,1,"n","j",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,23,1,"n","j",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,24,1,"n","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,1,1,"n","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,2,1,"n","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,3,1,"n","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,4,1,"n","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,5,1,"n","j",0,null,null,16,null,null,{"$f":"IF(($L122-$I122)/(($C$4-$C$16))>=O$21,1*$F122,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,6,1,"n","j",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,7,1,"n","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,8,1,"n","j",-0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,9,1,"n","j",-0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,10,1,"n","j",0,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,11,1,"n","j",-0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,12,1,"n","j",-0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,13,1,"n","j",0.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,14,1,"n","j",1.6,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,15,1,"n","j",2,null,null,17,null,null,{"$f":"IF(($L132-$I132)/(($C$4-$C$16))>=O$21,1*$F132,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,16,1,"n","j",2.1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,17,1,"n","j",1.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,18,1,"n","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,19,1,"n","j",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,20,1,"n","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,21,1,"n","j",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,22,1,"n","j",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,23,1,"n","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,24,1,"n","j",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,1,1,"n","n",-0.8,null,null,16,null,null,{"$f":"IF(($L142-$I142)/(($C$4-$C$16))>=O$21,1*$F142,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,6,6,2,1,"n","n",-0.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,6,3,1,"n","n",-1.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,6,4,1,"n","n",-2.2999999999999998,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,6,5,1,"n","n",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,6,6,1,"n","n",-3.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,6,7,1,"n","n",-3.8,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,6,8,1,"n","n",-4.0999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,6,9,1,"n","n",-4.3,null,null,{"$f":"IF(AND(H150=\"j\",OR(AND($C$9<=E150,E150<$C$10),AND($D$9<=E150,E150<$D$10))),$J$5,$C$5)*F150","v":16},null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,6,10,{"$f":"IF(AND(B151>$D$13,B151<$I$13),0,IF(B151=$D$13,IF(D151>=$D$12,0,1),IF(B151=$I$13,IF(D151<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C151=7),AND($I$9=1,C151>5)),\"n\",IF($I$9=2,G151,\"j\"))","v":"n"},-4.0999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,6,11,1,"n","n",-3.5,null,null,16,null,null,{"$f":"IF(($L152-$I152)/(($C$4-$C$16))>=O$21,1*$F152,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,6,6,12,1,"n","n",-2.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,6,13,1,"n","n",-1.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,6,14,1,"n","n",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,6,15,1,"n","n",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,6,16,1,"n","n",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,6,17,1,"n","n",-1.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,6,18,1,"n","n",-3.2,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,6,19,1,"n","n",-3.6,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,6,20,1,"n","n",-3.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,6,21,1,"n","n",-4.4000000000000004,null,null,16,null,null,{"$f":"IF(($L162-$I162)/(($C$4-$C$16))>=O$21,1*$F162,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,6,6,22,1,"n","n",-5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,6,23,1,"n","n",-5.6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,6,6,24,1,"n","n",-5.7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,1,1,"n","n",-5.4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,7,2,1,"n","n",-5.0999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,7,3,1,"n","n",-4.9000000000000004,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,7,4,1,"n","n",-5.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,7,5,1,"n","n",-5.9,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,6,1,"n","n",-6.2,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,7,1,"n","n",-6.8,null,null,16,null,null,{"$f":"IF(($L172-$I172)/(($C$4-$C$16))>=O$21,1*$F172,0)","v":0},0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,8,1,"n","n",-7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,9,1,"n","n",-7.6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,10,1,"n","n",-8.3000000000000007,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,7,11,1,"n","n",-8.4,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,7,12,1,"n","n",-7.7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,13,1,"n","n",-6.5,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,14,1,"n","n",-6.3,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,15,1,"n","n",-6.4,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,16,1,"n","n",-6.3,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,17,1,"n","n",-6.8,null,null,16,null,null,{"$f":"IF(($L182-$I182)/(($C$4-$C$16))>=O$21,1*$F182,0)","v":0},0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,18,1,"n","n",-7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,19,1,"n","n",-6.5,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,20,1,"n","n",-6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,7,21,1,"n","n",-5.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,7,22,1,"n","n",-5.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,7,23,1,"n","n",-5.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,7,24,1,"n","n",-5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,1,1,"j","j",-5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,2,1,"j","j",-5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,3,1,"j","j",-5.0999999999999996,null,null,16,null,null,{"$f":"IF(($L192-$I192)/(($C$4-$C$16))>=O$21,1*$F192,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,4,1,"j","j",-5.2,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,5,1,"j","j",-5.0999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,6,1,"j","j",-5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,7,1,"j","j",-4.9000000000000004,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,8,1,"j","j",-5.3,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,1,8,9,1,"j","j",-5.7,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,1,8,10,1,"j","j",-5.6,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,1,8,11,1,"j","j",-5.3,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,1,8,12,1,"j","j",-5,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,1,8,13,1,"j","j",-4.5999999999999996,null,null,17,null,null,{"$f":"IF(($L202-$I202)/(($C$4-$C$16))>=O$21,1*$F202,0)","v":0},0,1,1,1,1,1,1,1,1,1]
[null,1,1,8,14,1,"j","j",-3.9,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,15,1,"j","j",-3.8,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,16,1,"j","j",-3.7,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,17,1,"j","j",-3.7,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,18,1,"j","j",-3.8,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,19,1,"j","j",-3.7,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,20,1,"j","j",-3.6,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,21,1,"j","j",-3.6,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,22,1,"j","j",-4.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,8,23,1,"j","j",-5.6,null,null,16,null,null,{"$f":"IF(($L212-$I212)/(($C$4-$C$16))>=O$21,1*$F212,0)","v":0},0,1,1,1,1,1,1,1,1,1]
[null,1,1,8,24,1,"j","j",-6.7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,2,9,1,1,"j","j",-7.7,null,null,{"$f":"IF(AND(H214=\"j\",OR(AND($C$9<=E214,E214<$C$10),AND($D$9<=E214,E214<$D$10))),$J$5,$C$5)*F214","v":16},null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,2,9,2,{"$f":"IF(AND(B215>$D$13,B215<$I$13),0,IF(B215=$D$13,IF(D215>=$D$12,0,1),IF(B215=$I$13,IF(D215<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C215=7),AND($I$9=1,C215>5)),\"n\",IF($I$9=2,G215,\"j\"))","v":"j"},-7.9,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,2,9,3,1,"j","j",-8.6,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,9,4,1,"j","j",-9.1,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,9,5,1,"j","j",-9.1999999999999993,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,9,6,1,"j","j",-8.5,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,9,7,1,"j","j",-7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,2,9,8,1,"j","j",-5.5,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,2,9,9,1,"j","j",-4.8,null,null,17,null,null,{"$f":"IF(($L222-$I222)/(($C$4-$C$16))>=O$21,1*$F222,0)","v":0},0,1,1,1,1,1,1,1,1,1]
[null,1,2,9,10,1,"j","j",-4.5,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,11,1,"j","j",-4.2,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,12,1,"j","j",-4.2,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,13,1,"j","j",-3.6,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,14,1,"j","j",-3,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,15,1,"j","j",-2.4,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,16,1,"j","j",-2.2999999999999998,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,17,1,"j","j",-3.7,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,18,1,"j","j",-5.4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,19,1,"j","j",-5.3,null,null,16,null,null,{"$f":"IF(($L232-$I232)/(($C$4-$C$16))>=O$21,1*$F232,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,20,1,"j","j",-4.0999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,21,1,"j","j",-3.1,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,22,1,"j","j",-2.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,23,1,"j","j",-3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,24,1,"j","j",-3.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,1,1,"j","j",-3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,2,1,"j","j",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,3,1,"j","j",-2.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,4,1,"j","j",-2.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,5,1,"j","j",-2,null,null,16,null,null,{"$f":"IF(($L242-$I242)/(($C$4-$C$16))>=O$21,1*$F242,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,6,1,"j","j",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,7,1,"j","j",-1.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,8,1,"j","j",-2,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,9,1,"j","j",-1.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,10,1,"j","j",-1.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,11,1,"j","j",-1.1000000000000001,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,12,1,"j","j",-0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,13,1,"j","j",-0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,14,1,"j","j",-0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,15,1,"j","j",-0.6,null,null,17,null,null,{"$f":"IF(($L252-$I252)/(($C$4-$C$16))>=O$21,1*$F252,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,16,1,"j","j",-0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,17,1,"j","j",-1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,18,1,"j","j",-0.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,19,1,"j","j",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,20,1,"j","j",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,21,1,"j","j",-0.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,22,1,"j","j",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,23,1,"j","j",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,10,24,1,"j","j",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,11,1,1,"j","j",-0.5,null,null,16,null,null,{"$f":"IF(($L262-$I262)/(($C$4-$C$16))>=O$21,1*$F262,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,4,11,2,1,"j","j",-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,11,3,1,"j","j",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,11,4,1,"j","j",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,11,5,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,11,6,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,11,7,1,"j","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,11,8,1,"j","j",0.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,11,9,1,"j","j",1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,11,10,1,"j","j",1.3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,11,11,1,"j","j",1.6,null,null,17,null,null,{"$f":"IF(($L272-$I272)/(($C$4-$C$16))>=O$21,1*$F272,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,4,11,12,1,"j","j",1.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,11,13,1,"j","j",2.2000000000000002,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,11,14,1,"j","j",2.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,11,15,1,"j","j",3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,11,16,1,"j","j",3.3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,11,17,1,"j","j",3.2,null,null,{"$f":"IF(AND(H278=\"j\",OR(AND($C$9<=E278,E278<$C$10),AND($D$9<=E278,E278<$D$10))),$J$5,$C$5)*F278","v":17},null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,11,18,{"$f":"IF(AND(B279>$D$13,B279<$I$13),0,IF(B279=$D$13,IF(D279>=$D$12,0,1),IF(B279=$I$13,IF(D279<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C279=7),AND($I$9=1,C279>5)),\"n\",IF($I$9=2,G279,\"j\"))","v":"j"},3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,11,19,1,"j","j",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,11,20,1,"j","j",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,11,21,1,"j","j",3.4,null,null,16,null,null,{"$f":"IF(($L282-$I282)/(($C$4-$C$16))>=O$21,1*$F282,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,4,11,22,1,"j","j",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,11,23,1,"j","j",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,11,24,1,"j","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,1,1,"j","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,2,1,"j","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,3,1,"j","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,4,1,"j","j",2.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,12,5,1,"j","j",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,12,6,1,"j","j",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,12,7,1,"j","j",2.2000000000000002,null,null,16,null,null,{"$f":"IF(($L292-$I292)/(($C$4-$C$16))>=O$21,1*$F292,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,5,12,8,1,"j","j",2.2000000000000002,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,12,9,1,"j","j",2.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,12,10,1,"j","j",2.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,12,11,1,"j","j",2.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,12,12,1,"j","j",3.1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,12,13,1,"j","j",3.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,14,1,"j","j",4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,15,1,"j","j",4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,16,1,"j","j",3.7,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,17,1,"j","j",3.5,null,null,17,null,null,{"$f":"IF(($L302-$I302)/(($C$4-$C$16))>=O$21,1*$F302,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,5,12,18,1,"j","j",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,19,1,"j","j",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,20,1,"j","j",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,21,1,"j","j",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,22,1,"j","j",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,23,1,"j","j",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,12,24,1,"j","j",4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,1,1,"j","n",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,2,1,"j","n",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,3,1,"j","n",4.7,null,null,16,null,null,{"$f":"IF(($L312-$I312)/(($C$4-$C$16))>=O$21,1*$F312,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,4,1,"j","n",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,5,1,"j","n",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,6,1,"j","n",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,7,1,"j","n",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,8,1,"j","n",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,9,1,"j","n",4.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,10,1,"j","n",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,11,1,"j","n",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,12,1,"j","n",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,13,1,"j","n",5.0999999999999996,null,null,16,null,null,{"$f":"IF(($L322-$I322)/(($C$4-$C$16))>=O$21,1*$F322,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,6,13,14,1,"j","n",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,13,15,1,"j","n",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,13,16,1,"j","n",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,13,17,1,"j","n",6.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,13,18,1,"j","n",6.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,13,19,1,"j","n",6.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,13,20,1,"j","n",6.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,13,21,1,"j","n",6.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,13,22,1,"j","n",6.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,13,23,1,"j","n",6.2,null,null,16,null,null,{"$f":"IF(($L332-$I332)/(($C$4-$C$16))>=O$21,1*$F332,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,1,6,13,24,1,"j","n",6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,1,1,"j","n",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,2,1,"j","n",6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,3,1,"j","n",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,4,1,"j","n",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,5,1,"j","n",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,6,1,"j","n",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,7,1,"j","n",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,8,1,"j","n",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,9,1,"j","n",5.4,null,null,{"$f":"IF(AND(H342=\"j\",OR(AND($C$9<=E342,E342<$C$10),AND($D$9<=E342,E342<$D$10))),$J$5,$C$5)*F342","v":16},null,null,{"$f":"IF(($L342-$I342)/(($C$4-$C$16))>=O$21,1*$F342,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,10,{"$f":"IF(AND(B343>$D$13,B343<$I$13),0,IF(B343=$D$13,IF(D343>=$D$12,0,1),IF(B343=$I$13,IF(D343<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C343=7),AND($I$9=1,C343>5)),\"n\",IF($I$9=2,G343,\"j\"))","v":"n"},5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,11,1,"j","n",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,12,1,"j","n",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,13,1,"j","n",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,14,1,"j","n",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,15,1,"j","n",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,16,1,"j","n",6.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,17,1,"j","n",6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,18,1,"j","n",6.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,19,1,"j","n",6.2,null,null,16,null,null,{"$f":"IF(($L352-$I352)/(($C$4-$C$16))>=O$21,1*$F352,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,20,1,"j","n",6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,21,1,"j","n",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,22,1,"j","n",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,23,1,"j","n",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,14,24,1,"j","n",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,1,1,"j","j",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,2,1,"j","j",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,3,1,"j","j",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,4,1,"j","j",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,5,1,"j","j",4.3,null,null,16,null,null,{"$f":"IF(($L362-$I362)/(($C$4-$C$16))>=O$21,1*$F362,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,6,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,7,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,8,1,"j","j",4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,9,1,"j","j",4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,10,1,"j","j",4.0999999999999996,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,11,1,"j","j",4.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,12,1,"j","j",4.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,13,1,"j","j",4.4000000000000004,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,14,1,"j","j",4.7,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,15,1,"j","j",4.9000000000000004,null,null,17,null,null,{"$f":"IF(($L372-$I372)/(($C$4-$C$16))>=O$21,1*$F372,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,16,1,"j","j",4.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,17,1,"j","j",4.7,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,18,1,"j","j",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,19,1,"j","j",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,20,1,"j","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,21,1,"j","j",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,22,1,"j","j",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,23,1,"j","j",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,15,24,1,"j","j",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,16,1,1,"j","j",3.1,null,null,16,null,null,{"$f":"IF(($L382-$I382)/(($C$4-$C$16))>=O$21,1*$F382,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,2,16,2,1,"j","j",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,16,3,1,"j","j",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,16,4,1,"j","j",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,16,5,1,"j","j",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,16,6,1,"j","j",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,16,7,1,"j","j",2.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,16,8,1,"j","j",2.2999999999999998,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,16,9,1,"j","j",1.6,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,16,10,1,"j","j",0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,16,11,1,"j","j",0.5,null,null,17,null,null,{"$f":"IF(($L392-$I392)/(($C$4-$C$16))>=O$21,1*$F392,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,2,16,12,1,"j","j",0.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,16,13,1,"j","j",1.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,16,14,1,"j","j",2.1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,16,15,1,"j","j",2.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,16,16,1,"j","j",3.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,16,17,1,"j","j",4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,16,18,1,"j","j",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,16,19,1,"j","j",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,16,20,1,"j","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,16,21,1,"j","j",3,null,null,16,null,null,{"$f":"IF(($L402-$I402)/(($C$4-$C$16))>=O$21,1*$F402,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,2,16,22,1,"j","j",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,16,23,1,"j","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,16,24,1,"j","j",0.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,17,1,1,"j","j",-0.4,null,null,{"$f":"IF(AND(H406=\"j\",OR(AND($C$9<=E406,E406<$C$10),AND($D$9<=E406,E406<$D$10))),$J$5,$C$5)*F406","v":16},null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,17,2,{"$f":"IF(AND(B407>$D$13,B407<$I$13),0,IF(B407=$D$13,IF(D407>=$D$12,0,1),IF(B407=$I$13,IF(D407<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C407=7),AND($I$9=1,C407>5)),\"n\",IF($I$9=2,G407,\"j\"))","v":"j"},-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,17,3,1,"j","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,17,4,1,"j","j",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,17,5,1,"j","j",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,17,6,1,"j","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,17,7,1,"j","j",-0.4,null,null,16,null,null,{"$f":"IF(($L412-$I412)/(($C$4-$C$16))>=O$21,1*$F412,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,3,17,8,1,"j","j",-0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,17,9,1,"j","j",-0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,17,10,1,"j","j",0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,17,11,1,"j","j",1.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,17,12,1,"j","j",2.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,17,13,1,"j","j",4.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,17,14,1,"j","j",5.5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,17,15,1,"j","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,17,16,1,"j","j",5.4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,17,17,1,"j","j",4,null,null,17,null,null,{"$f":"IF(($L422-$I422)/(($C$4-$C$16))>=O$21,1*$F422,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,3,17,18,1,"j","j",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,17,19,1,"j","j",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,17,20,1,"j","j",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,17,21,1,"j","j",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,17,22,1,"j","j",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,17,23,1,"j","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,17,24,1,"j","j",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,18,1,1,"j","j",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,18,2,1,"j","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,18,3,1,"j","j",1.2,null,null,16,null,null,{"$f":"IF(($L432-$I432)/(($C$4-$C$16))>=O$21,1*$F432,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,4,18,4,1,"j","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,18,5,1,"j","j",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,18,6,1,"j","j",2.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,18,7,1,"j","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,18,8,1,"j","j",2.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,18,9,1,"j","j",3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,18,10,1,"j","j",3.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,18,11,1,"j","j",3.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,18,12,1,"j","j",4.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,18,13,1,"j","j",4.7,null,null,17,null,null,{"$f":"IF(($L442-$I442)/(($C$4-$C$16))>=O$21,1*$F442,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,4,18,14,1,"j","j",5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,18,15,1,"j","j",5.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,18,16,1,"j","j",5.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,18,17,1,"j","j",5.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,18,18,1,"j","j",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,18,19,1,"j","j",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,18,20,1,"j","j",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,18,21,1,"j","j",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,18,22,1,"j","j",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,18,23,1,"j","j",5.2,null,null,16,null,null,{"$f":"IF(($L452-$I452)/(($C$4-$C$16))>=O$21,1*$F452,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,4,18,24,1,"j","j",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,1,1,"j","j",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,2,1,"j","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,3,1,"j","j",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,4,1,"j","j",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,19,5,1,"j","j",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,6,1,"j","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,7,1,"j","j",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,8,1,"j","j",5.4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,19,9,1,"j","j",5.0999999999999996,null,null,17,null,null,{"$f":"IF(($L462-$I462)/(($C$4-$C$16))>=O$21,1*$F462,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,5,19,10,1,"j","j",5.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,19,11,1,"j","j",5.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,19,12,1,"j","j",6.7,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,13,1,"j","j",7.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,14,1,"j","j",7.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,15,1,"j","j",7.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,16,1,"j","j",7.2,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,17,1,"j","j",6.8,null,null,{"$f":"IF(AND(H470=\"j\",OR(AND($C$9<=E470,E470<$C$10),AND($D$9<=E470,E470<$D$10))),$J$5,$C$5)*F470","v":17},null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,18,{"$f":"IF(AND(B471>$D$13,B471<$I$13),0,IF(B471=$D$13,IF(D471>=$D$12,0,1),IF(B471=$I$13,IF(D471<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C471=7),AND($I$9=1,C471>5)),\"n\",IF($I$9=2,G471,\"j\"))","v":"j"},6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,19,1,"j","j",6,null,null,16,null,null,{"$f":"IF(($L472-$I472)/(($C$4-$C$16))>=O$21,1*$F472,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,20,1,"j","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,21,1,"j","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,22,1,"j","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,23,1,"j","j",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,19,24,1,"j","j",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,20,1,1,"j","n",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,20,2,1,"j","n",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,20,3,1,"j","n",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,20,4,1,"j","n",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,20,5,1,"j","n",2.2000000000000002,null,null,16,null,null,{"$f":"IF(($L482-$I482)/(($C$4-$C$16))>=O$21,1*$F482,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,6,20,6,1,"j","n",2.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,20,7,1,"j","n",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,20,8,1,"j","n",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,20,9,1,"j","n",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,20,10,1,"j","n",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,20,11,1,"j","n",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,20,12,1,"j","n",6.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,20,13,1,"j","n",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,20,14,1,"j","n",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,20,15,1,"j","n",8.6999999999999993,null,null,16,null,null,{"$f":"IF(($L492-$I492)/(($C$4-$C$16))>=O$21,1*$F492,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,1,6,20,16,1,"j","n",8.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,20,17,1,"j","n",8.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,20,18,1,"j","n",7.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,20,19,1,"j","n",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,20,20,1,"j","n",8.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,20,21,1,"j","n",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,20,22,1,"j","n",8.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,20,23,1,"j","n",8.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,20,24,1,"j","n",8.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,21,1,1,"j","n",8.5,null,null,16,null,null,{"$f":"IF(($L502-$I502)/(($C$4-$C$16))>=O$21,1*$F502,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,1,7,21,2,1,"j","n",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,21,3,1,"j","n",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,21,4,1,"j","n",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,21,5,1,"j","n",8.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,21,6,1,"j","n",7.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,21,7,1,"j","n",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,21,8,1,"j","n",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,21,9,1,"j","n",7.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,21,10,1,"j","n",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,21,11,1,"j","n",7.5,null,null,16,null,null,{"$f":"IF(($L512-$I512)/(($C$4-$C$16))>=O$21,1*$F512,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,1,7,21,12,1,"j","n",7.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,21,13,1,"j","n",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,21,14,1,"j","n",8.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,21,15,1,"j","n",8.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,21,16,1,"j","n",8.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,21,17,1,"j","n",8.6999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,21,18,1,"j","n",8.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,21,19,1,"j","n",8.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,21,20,1,"j","n",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,21,21,1,"j","n",7.3,null,null,16,null,null,{"$f":"IF(($L522-$I522)/(($C$4-$C$16))>=O$21,1*$F522,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,1,7,21,22,1,"j","n",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,21,23,1,"j","n",6.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,7,21,24,1,"j","n",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,1,22,1,1,"j","j",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,2,1,"j","j",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,3,1,"j","j",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,4,1,"j","j",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,5,1,"j","j",2.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,6,1,"j","j",2.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,7,1,"j","j",2.2000000000000002,null,null,16,null,null,{"$f":"IF(($L532-$I532)/(($C$4-$C$16))>=O$21,1*$F532,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,8,1,"j","j",2.2999999999999998,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,9,1,"j","j",2.4,null,null,{"$f":"IF(AND(H534=\"j\",OR(AND($C$9<=E534,E534<$C$10),AND($D$9<=E534,E534<$D$10))),$J$5,$C$5)*F534","v":17},null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,10,{"$f":"IF(AND(B535>$D$13,B535<$I$13),0,IF(B535=$D$13,IF(D535>=$D$12,0,1),IF(B535=$I$13,IF(D535<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C535=7),AND($I$9=1,C535>5)),\"n\",IF($I$9=2,G535,\"j\"))","v":"j"},2.6,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,11,1,"j","j",3.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,12,1,"j","j",5.0999999999999996,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,13,1,"j","j",4.9000000000000004,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,14,1,"j","j",5.5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,15,1,"j","j",6.1,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,16,1,"j","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,17,1,"j","j",5.9,null,null,17,null,null,{"$f":"IF(($L542-$I542)/(($C$4-$C$16))>=O$21,1*$F542,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,18,1,"j","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,1,22,19,1,"j","j",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,20,1,"j","j",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,21,1,"j","j",4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,22,1,"j","j",4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,23,1,"j","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,1,22,24,1,"j","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,1,1,"j","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,2,1,"j","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,3,1,"j","j",3.7,null,null,16,null,null,{"$f":"IF(($L552-$I552)/(($C$4-$C$16))>=O$21,1*$F552,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,4,1,"j","j",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,5,1,"j","j",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,6,1,"j","j",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,7,1,"j","j",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,8,1,"j","j",3.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,9,1,"j","j",3.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,10,1,"j","j",4.4000000000000004,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,11,1,"j","j",4.5999999999999996,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,12,1,"j","j",4.4000000000000004,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,13,1,"j","j",4.3,null,null,17,null,null,{"$f":"IF(($L562-$I562)/(($C$4-$C$16))>=O$21,1*$F562,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,14,1,"j","j",4.5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,15,1,"j","j",5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,16,1,"j","j",5.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,17,1,"j","j",6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,18,1,"j","j",6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,2,23,19,1,"j","j",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,2,23,20,1,"j","j",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,2,23,21,1,"j","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,2,23,22,1,"j","j",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,23,1,"j","j",4.5,null,null,16,null,null,{"$f":"IF(($L572-$I572)/(($C$4-$C$16))>=O$21,1*$F572,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,2,23,24,1,"j","j",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,24,1,1,"j","j",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,2,1,"j","j",6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,3,1,"j","j",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,4,1,"j","j",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,24,5,1,"j","j",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,24,6,1,"j","j",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,24,7,1,"j","j",4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,24,8,1,"j","j",4.5999999999999996,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,24,9,1,"j","j",5.4,null,null,17,null,null,{"$f":"IF(($L582-$I582)/(($C$4-$C$16))>=O$21,1*$F582,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,3,24,10,1,"j","j",5.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,24,11,1,"j","j",5.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,24,12,1,"j","j",6.3,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,13,1,"j","j",6.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,14,1,"j","j",6.9,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,15,1,"j","j",7.2,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,16,1,"j","j",7.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,17,1,"j","j",7.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,18,1,"j","j",7.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,19,1,"j","j",7.3,null,null,16,null,null,{"$f":"IF(($L592-$I592)/(($C$4-$C$16))>=O$21,1*$F592,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,20,1,"j","j",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,21,1,"j","j",6.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,22,1,"j","j",6.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,23,1,"j","j",6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,24,24,1,"j","j",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,1,1,"j","j",5.4,null,null,{"$f":"IF(AND(H598=\"j\",OR(AND($C$9<=E598,E598<$C$10),AND($D$9<=E598,E598<$D$10))),$J$5,$C$5)*F598","v":16},null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,2,{"$f":"IF(AND(B599>$D$13,B599<$I$13),0,IF(B599=$D$13,IF(D599>=$D$12,0,1),IF(B599=$I$13,IF(D599<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C599=7),AND($I$9=1,C599>5)),\"n\",IF($I$9=2,G599,\"j\"))","v":"j"},5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,3,1,"j","j",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,4,1,"j","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,5,1,"j","j",5.8,null,null,16,null,null,{"$f":"IF(($L602-$I602)/(($C$4-$C$16))>=O$21,1*$F602,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,6,1,"j","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,7,1,"j","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,8,1,"j","j",5.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,25,9,1,"j","j",5.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,25,10,1,"j","j",5.7,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,25,11,1,"j","j",6.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,4,25,12,1,"j","j",6.8,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,13,1,"j","j",7.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,14,1,"j","j",7.9,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,15,1,"j","j",8,null,null,17,null,null,{"$f":"IF(($L612-$I612)/(($C$4-$C$16))>=O$21,1*$F612,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,16,1,"j","j",8.1999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,17,1,"j","j",8.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,18,1,"j","j",9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,4,25,19,1,"j","j",8.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,4,25,20,1,"j","j",8.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,4,25,21,1,"j","j",7.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,22,1,"j","j",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,23,1,"j","j",6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,4,25,24,1,"j","j",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,1,1,"j","j",6.5,null,null,16,null,null,{"$f":"IF(($L622-$I622)/(($C$4-$C$16))>=O$21,1*$F622,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,2,1,"j","j",6.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,3,1,"j","j",6.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,4,1,"j","j",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,5,1,"j","j",7.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,6,1,"j","j",7.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,7,1,"j","j",7.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,8,1,"j","j",7.2,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,9,1,"j","j",7.1,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,10,1,"j","j",7.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,11,1,"j","j",8.4,null,null,17,null,null,{"$f":"IF(($L632-$I632)/(($C$4-$C$16))>=O$21,1*$F632,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,12,1,"j","j",8.8000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,13,1,"j","j",8.9,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,14,1,"j","j",8.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,15,1,"j","j",8.8000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,16,1,"j","j",8.9,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,17,1,"j","j",8.3000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,18,1,"j","j",7.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,19,1,"j","j",6.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,20,1,"j","j",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,5,26,21,1,"j","j",5,null,null,16,null,null,{"$f":"IF(($L642-$I642)/(($C$4-$C$16))>=O$21,1*$F642,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,5,26,22,1,"j","j",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,26,23,1,"j","j",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,5,26,24,1,"j","j",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,27,1,1,"j","n",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,27,2,1,"j","n",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,27,3,1,"j","n",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,27,4,1,"j","n",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,27,5,1,"j","n",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,6,27,6,1,"j","n",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,27,7,1,"j","n",5.7,null,null,16,null,null,{"$f":"IF(($L652-$I652)/(($C$4-$C$16))>=O$21,1*$F652,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,1,6,27,8,1,"j","n",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,27,9,1,"j","n",6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,27,10,1,"j","n",6.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,27,11,1,"j","n",7.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,27,12,1,"j","n",7.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,6,27,13,1,"j","n",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,27,14,1,"j","n",8.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,27,15,1,"j","n",9.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,27,16,1,"j","n",10,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,27,17,1,"j","n",10.199999999999999,null,null,{"$f":"IF(AND(H662=\"j\",OR(AND($C$9<=E662,E662<$C$10),AND($D$9<=E662,E662<$D$10))),$J$5,$C$5)*F662","v":16},null,null,{"$f":"IF(($L662-$I662)/(($C$4-$C$16))>=O$21,1*$F662,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,1,6,27,18,{"$f":"IF(AND(B663>$D$13,B663<$I$13),0,IF(B663=$D$13,IF(D663>=$D$12,0,1),IF(B663=$I$13,IF(D663<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C663=7),AND($I$9=1,C663>5)),\"n\",IF($I$9=2,G663,\"j\"))","v":"n"},10.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,27,19,1,"j","n",10.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,27,20,1,"j","n",10.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,27,21,1,"j","n",10.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,6,27,22,1,"j","n",10.199999999999999,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,27,23,1,"j","n",10,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,6,27,24,1,"j","n",10.199999999999999,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,28,1,1,"j","n",10.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,28,2,1,"j","n",10.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,28,3,1,"j","n",10.199999999999999,null,null,16,null,null,{"$f":"IF(($L672-$I672)/(($C$4-$C$16))>=O$21,1*$F672,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,1,7,28,4,1,"j","n",10.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,28,5,1,"j","n",9.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,28,6,1,"j","n",9.6999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,28,7,1,"j","n",9.6999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,28,8,1,"j","n",9.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,28,9,1,"j","n",10,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,28,10,1,"j","n",10.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,28,11,1,"j","n",11.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,7,28,12,1,"j","n",11.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,7,28,13,1,"j","n",11.9,null,null,16,null,null,{"$f":"IF(($L682-$I682)/(($C$4-$C$16))>=O$21,1*$F682,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,1,7,28,14,1,"j","n",12.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,7,28,15,1,"j","n",12.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,7,28,16,1,"j","n",13,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,7,28,17,1,"j","n",12.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,7,28,18,1,"j","n",11.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,7,28,19,1,"j","n",11.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,7,28,20,1,"j","n",10.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,7,28,21,1,"j","n",10.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,28,22,1,"j","n",10.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,7,28,23,1,"j","n",10.7,null,null,16,null,null,{"$f":"IF(($L692-$I692)/(($C$4-$C$16))>=O$21,1*$F692,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,1,7,28,24,1,"j","n",10.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,1,29,1,1,"j","j",10.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,1,29,2,1,"j","j",10.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,3,1,"j","j",10.199999999999999,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,4,1,"j","j",10.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,5,1,"j","j",9.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,6,1,"j","j",9.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,7,1,"j","j",9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,8,1,"j","j",8.8000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,1,29,9,1,"j","j",9,null,null,17,null,null,{"$f":"IF(($L702-$I702)/(($C$4-$C$16))>=O$21,1*$F702,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,10,1,"j","j",9.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,11,1,"j","j",10.3,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,12,1,"j","j",11.4,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,13,1,"j","j",12.7,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,1,29,14,1,"j","j",13.4,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,1,29,15,1,"j","j",14,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,1,29,16,1,"j","j",14.4,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,1,1,29,17,1,"j","j",13.6,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,1,29,18,1,"j","j",11.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,1,29,19,1,"j","j",10.7,null,null,16,null,null,{"$f":"IF(($L712-$I712)/(($C$4-$C$16))>=O$21,1*$F712,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,1,1,29,20,1,"j","j",10.199999999999999,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,21,1,"j","j",9.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,22,1,"j","j",9.6999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,23,1,"j","j",9.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,1,29,24,1,"j","j",9.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,2,30,1,1,"j","j",9.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,2,30,2,1,"j","j",9.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,2,30,3,1,"j","j",9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,2,30,4,1,"j","j",8.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,2,30,5,1,"j","j",8.9,null,null,16,null,null,{"$f":"IF(($L722-$I722)/(($C$4-$C$16))>=O$21,1*$F722,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,1,2,30,6,1,"j","j",8.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,2,30,7,1,"j","j",7.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,2,30,8,1,"j","j",6.8,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,2,30,9,1,"j","j",7.3,null,null,{"$f":"IF(AND(H726=\"j\",OR(AND($C$9<=E726,E726<$C$10),AND($D$9<=E726,E726<$D$10))),$J$5,$C$5)*F726","v":17},null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,2,30,10,{"$f":"IF(AND(B727>$D$13,B727<$I$13),0,IF(B727=$D$13,IF(D727>=$D$12,0,1),IF(B727=$I$13,IF(D727<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C727=7),AND($I$9=1,C727>5)),\"n\",IF($I$9=2,G727,\"j\"))","v":"j"},7.9,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,2,30,11,1,"j","j",8.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,2,30,12,1,"j","j",9.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,2,30,13,1,"j","j",11.7,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,2,30,14,1,"j","j",12.9,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,2,30,15,1,"j","j",12.9,null,null,17,null,null,{"$f":"IF(($L732-$I732)/(($C$4-$C$16))>=O$21,1*$F732,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,1,2,30,16,1,"j","j",12.8,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,2,30,17,1,"j","j",12,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,2,30,18,1,"j","j",11,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,2,30,19,1,"j","j",11.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,2,30,20,1,"j","j",11.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,2,30,21,1,"j","j",11.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,2,30,22,1,"j","j",11.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,2,30,23,1,"j","j",11.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,2,30,24,1,"j","j",10.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,1,3,31,1,1,"j","j",10.3,null,null,16,null,null,{"$f":"IF(($L742-$I742)/(($C$4-$C$16))>=O$21,1*$F742,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,2,1,"j","j",10,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,3,1,"j","j",8.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,4,1,"j","j",8.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,5,1,"j","j",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,6,1,"j","j",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,31,7,1,"j","j",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,31,8,1,"j","j",7.8,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,31,9,1,"j","j",7.9,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,31,10,1,"j","j",8.1,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,31,11,1,"j","j",8.9,null,null,17,null,null,{"$f":"IF(($L752-$I752)/(($C$4-$C$16))>=O$21,1*$F752,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,1,3,31,12,1,"j","j",9.6,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,13,1,"j","j",9.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,14,1,"j","j",9.8000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,15,1,"j","j",10.3,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,16,1,"j","j",10.5,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,17,1,"j","j",10,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,18,1,"j","j",9.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,19,1,"j","j",9.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,20,1,"j","j",9.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,21,1,"j","j",9.3000000000000007,null,null,16,null,null,{"$f":"IF(($L762-$I762)/(($C$4-$C$16))>=O$21,1*$F762,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,22,1,"j","j",8.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,23,1,"j","j",8.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,1,3,31,24,1,"j","j",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,4,1,1,1,"j","j",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,2,1,"j","j",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,1,3,1,"j","j",-2.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,1,4,1,"j","j",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,2,4,1,5,1,"j","j",-2.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,1,6,1,"j","j",-2.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,1,7,1,"j","j",-2.2999999999999998,null,null,16,null,null,{"$f":"IF(($L772-$I772)/(($C$4-$C$16))>=O$21,1*$F772,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,2,4,1,8,1,"j","j",-2.2000000000000002,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,2,4,1,9,1,"j","j",-1.6,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,1,10,1,"j","j",-1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,1,11,1,"j","j",-0.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,1,12,1,"j","j",0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,1,13,1,"j","j",1.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,1,14,1,"j","j",2.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,1,15,1,"j","j",3.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,1,16,1,"j","j",3.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,17,1,"j","j",3.5,null,null,17,null,null,{"$f":"IF(($L782-$I782)/(($C$4-$C$16))>=O$21,1*$F782,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,4,1,18,1,"j","j",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,19,1,"j","j",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,20,1,"j","j",2.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,1,21,1,"j","j",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,1,22,1,"j","j",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,1,23,1,"j","j",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,1,24,1,"j","j",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,1,1,"j","j",0.8,null,null,{"$f":"IF(AND(H790=\"j\",OR(AND($C$9<=E790,E790<$C$10),AND($D$9<=E790,E790<$D$10))),$J$5,$C$5)*F790","v":16},null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,2,{"$f":"IF(AND(B791>$D$13,B791<$I$13),0,IF(B791=$D$13,IF(D791>=$D$12,0,1),IF(B791=$I$13,IF(D791<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C791=7),AND($I$9=1,C791>5)),\"n\",IF($I$9=2,G791,\"j\"))","v":"j"},0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,3,1,"j","j",0.3,null,null,16,null,null,{"$f":"IF(($L792-$I792)/(($C$4-$C$16))>=O$21,1*$F792,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,4,1,"j","j",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,5,1,"j","j",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,5,2,6,1,"j","j",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,5,2,7,1,"j","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,5,2,8,1,"j","j",0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,5,2,9,1,"j","j",0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,5,2,10,1,"j","j",0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,5,2,11,1,"j","j",1.1000000000000001,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,12,1,"j","j",1.6,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,13,1,"j","j",2.1,null,null,17,null,null,{"$f":"IF(($L802-$I802)/(($C$4-$C$16))>=O$21,1*$F802,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,14,1,"j","j",2.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,15,1,"j","j",3.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,16,1,"j","j",3.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,17,1,"j","j",3.7,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,18,1,"j","j",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,19,1,"j","j",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,20,1,"j","j",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,21,1,"j","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,22,1,"j","j",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,23,1,"j","j",1,null,null,16,null,null,{"$f":"IF(($L812-$I812)/(($C$4-$C$16))>=O$21,1*$F812,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,24,1,"j","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,1,1,"j","n",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,2,1,"j","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,3,1,"j","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,4,1,"j","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,5,1,"j","n",0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,6,1,"j","n",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,6,3,7,1,"j","n",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,6,3,8,1,"j","n",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,6,3,9,1,"j","n",0.1,null,null,16,null,null,{"$f":"IF(($L822-$I822)/(($C$4-$C$16))>=O$21,1*$F822,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,10,1,"j","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,11,1,"j","n",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,12,1,"j","n",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,13,1,"j","n",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,14,1,"j","n",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,15,1,"j","n",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,16,1,"j","n",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,17,1,"j","n",2.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,18,1,"j","n",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,19,1,"j","n",2.2000000000000002,null,null,16,null,null,{"$f":"IF(($L832-$I832)/(($C$4-$C$16))>=O$21,1*$F832,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,20,1,"j","n",2.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,21,1,"j","n",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,22,1,"j","n",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,23,1,"j","n",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,24,1,"j","n",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,1,1,"j","n",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,2,1,"j","n",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,3,1,"j","n",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,4,1,"j","n",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,5,1,"j","n",3.4,null,null,16,null,null,{"$f":"IF(($L842-$I842)/(($C$4-$C$16))>=O$21,1*$F842,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,6,1,"j","n",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,7,1,"j","n",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,8,1,"j","n",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,9,1,"j","n",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,10,1,"j","n",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,11,1,"j","n",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,12,1,"j","n",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,13,1,"j","n",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,7,4,14,1,"j","n",6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,7,4,15,1,"j","n",7.5,null,null,16,null,null,{"$f":"IF(($L852-$I852)/(($C$4-$C$16))>=O$21,1*$F852,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,2,7,4,16,1,"j","n",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,7,4,17,1,"j","n",6,null,null,{"$f":"IF(AND(H854=\"j\",OR(AND($C$9<=E854,E854<$C$10),AND($D$9<=E854,E854<$D$10))),$J$5,$C$5)*F854","v":16},null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,7,4,18,{"$f":"IF(AND(B855>$D$13,B855<$I$13),0,IF(B855=$D$13,IF(D855>=$D$12,0,1),IF(B855=$I$13,IF(D855<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C855=7),AND($I$9=1,C855>5)),\"n\",IF($I$9=2,G855,\"j\"))","v":"n"},5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,7,4,19,1,"j","n",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,20,1,"j","n",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,21,1,"j","n",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,22,1,"j","n",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,7,4,23,1,"j","n",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,7,4,24,1,"j","n",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,1,1,"j","j",6.6,null,null,16,null,null,{"$f":"IF(($L862-$I862)/(($C$4-$C$16))>=O$21,1*$F862,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,2,1,"j","j",7.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,3,1,"j","j",7.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,4,1,"j","j",8.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,1,5,5,1,"j","j",9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,1,5,6,1,"j","j",9.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,1,5,7,1,"j","j",9.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,1,5,8,1,"j","j",9.9,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,1,5,9,1,"j","j",9.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,1,5,10,1,"j","j",9,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,1,5,11,1,"j","j",8.6999999999999993,null,null,17,null,null,{"$f":"IF(($L872-$I872)/(($C$4-$C$16))>=O$21,1*$F872,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,12,1,"j","j",8.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,13,1,"j","j",8.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,14,1,"j","j",8.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,15,1,"j","j",8.1999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,16,1,"j","j",8,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,17,1,"j","j",7.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,18,1,"j","j",6.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,19,1,"j","j",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,20,1,"j","j",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,5,21,1,"j","j",4.9000000000000004,null,null,16,null,null,{"$f":"IF(($L882-$I882)/(($C$4-$C$16))>=O$21,1*$F882,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,2,1,5,22,1,"j","j",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,1,5,23,1,"j","j",4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,1,5,24,1,"j","j",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,1,1,"j","j",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,2,1,"j","j",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,3,1,"j","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,4,1,"j","j",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,5,1,"j","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,6,1,"j","j",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,7,1,"j","j",4.5999999999999996,null,null,16,null,null,{"$f":"IF(($L892-$I892)/(($C$4-$C$16))>=O$21,1*$F892,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,8,1,"j","j",4.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,9,1,"j","j",5.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,10,1,"j","j",5.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,11,1,"j","j",5.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,12,1,"j","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,13,1,"j","j",6.8,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,2,6,14,1,"j","j",7.7,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,2,6,15,1,"j","j",8.3000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,2,6,16,1,"j","j",8.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,2,6,17,1,"j","j",9.1999999999999993,null,null,17,null,null,{"$f":"IF(($L902-$I902)/(($C$4-$C$16))>=O$21,1*$F902,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,2,2,6,18,1,"j","j",9.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,2,6,19,1,"j","j",9.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,2,6,20,1,"j","j",9.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,2,6,21,1,"j","j",9.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,2,6,22,1,"j","j",9.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,2,6,23,1,"j","j",9.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,2,6,24,1,"j","j",9.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,3,7,1,1,"j","j",9.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,3,7,2,1,"j","j",9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,3,7,3,1,"j","j",8.9,null,null,16,null,null,{"$f":"IF(($L912-$I912)/(($C$4-$C$16))>=O$21,1*$F912,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,2,3,7,4,1,"j","j",8.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,3,7,5,1,"j","j",8.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,3,7,6,1,"j","j",8.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,3,7,7,1,"j","j",8.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,3,7,8,1,"j","j",8.1999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,9,1,"j","j",8.1,null,null,{"$f":"IF(AND(H918=\"j\",OR(AND($C$9<=E918,E918<$C$10),AND($D$9<=E918,E918<$D$10))),$J$5,$C$5)*F918","v":17},null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,10,{"$f":"IF(AND(B919>$D$13,B919<$I$13),0,IF(B919=$D$13,IF(D919>=$D$12,0,1),IF(B919=$I$13,IF(D919<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C919=7),AND($I$9=1,C919>5)),\"n\",IF($I$9=2,G919,\"j\"))","v":"j"},8.3000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,11,1,"j","j",8.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,12,1,"j","j",8.9,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,13,1,"j","j",9,null,null,17,null,null,{"$f":"IF(($L922-$I922)/(($C$4-$C$16))>=O$21,1*$F922,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,2,3,7,14,1,"j","j",8.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,15,1,"j","j",8.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,16,1,"j","j",8.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,17,1,"j","j",8.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,18,1,"j","j",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,3,7,19,1,"j","j",7.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,20,1,"j","j",7.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,21,1,"j","j",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,22,1,"j","j",6.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,23,1,"j","j",6.4,null,null,16,null,null,{"$f":"IF(($L932-$I932)/(($C$4-$C$16))>=O$21,1*$F932,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,2,3,7,24,1,"j","j",6.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,8,1,1,"j","j",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,8,2,1,"j","j",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,8,3,1,"j","j",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,8,4,1,"j","j",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,8,5,1,"j","j",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,8,6,1,"j","j",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,8,7,1,"j","j",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,8,8,1,"j","j",5.7,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,8,9,1,"j","j",5.7,null,null,17,null,null,{"$f":"IF(($L942-$I942)/(($C$4-$C$16))>=O$21,1*$F942,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,2,4,8,10,1,"j","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,8,11,1,"j","j",6.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,8,12,1,"j","j",6.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,8,13,1,"j","j",6.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,8,14,1,"j","j",6.7,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,8,15,1,"j","j",6.8,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,8,16,1,"j","j",7.1,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,8,17,1,"j","j",6.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,8,18,1,"j","j",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,8,19,1,"j","j",4.9000000000000004,null,null,16,null,null,{"$f":"IF(($L952-$I952)/(($C$4-$C$16))>=O$21,1*$F952,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,2,4,8,20,1,"j","j",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,8,21,1,"j","j",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,8,22,1,"j","j",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,8,23,1,"j","j",2.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,8,24,1,"j","j",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,9,1,1,"j","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,9,2,1,"j","j",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,9,3,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,9,4,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,9,5,1,"j","j",0.3,null,null,16,null,null,{"$f":"IF(($L962-$I962)/(($C$4-$C$16))>=O$21,1*$F962,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,5,9,6,1,"j","j",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,9,7,1,"j","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,9,8,1,"j","j",-0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,5,9,9,1,"j","j",-0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,5,9,10,1,"j","j",0,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,5,9,11,1,"j","j",1.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,9,12,1,"j","j",3.7,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,13,1,"j","j",5.5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,14,1,"j","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,15,1,"j","j",6.2,null,null,17,null,null,{"$f":"IF(($L972-$I972)/(($C$4-$C$16))>=O$21,1*$F972,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,16,1,"j","j",6.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,17,1,"j","j",6.1,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,18,1,"j","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,19,1,"j","j",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,20,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,21,1,"j","j",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,22,1,"j","j",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,23,1,"j","j",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,9,24,1,"j","j",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,10,1,1,"j","n",1.6,null,null,{"$f":"IF(AND(H982=\"j\",OR(AND($C$9<=E982,E982<$C$10),AND($D$9<=E982,E982<$D$10))),$J$5,$C$5)*F982","v":16},null,null,{"$f":"IF(($L982-$I982)/(($C$4-$C$16))>=O$21,1*$F982,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,6,10,2,{"$f":"IF(AND(B983>$D$13,B983<$I$13),0,IF(B983=$D$13,IF(D983>=$D$12,0,1),IF(B983=$I$13,IF(D983<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C983=7),AND($I$9=1,C983>5)),\"n\",IF($I$9=2,G983,\"j\"))","v":"n"},1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,10,3,1,"j","n",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,10,4,1,"j","n",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,10,5,1,"j","n",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,10,6,1,"j","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,10,7,1,"j","n",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,10,8,1,"j","n",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,10,9,1,"j","n",2.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,10,10,1,"j","n",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,11,1,"j","n",4,null,null,16,null,null,{"$f":"IF(($L992-$I992)/(($C$4-$C$16))>=O$21,1*$F992,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,12,1,"j","n",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,13,1,"j","n",4.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,14,1,"j","n",4.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,15,1,"j","n",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,16,1,"j","n",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,17,1,"j","n",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,18,1,"j","n",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,19,1,"j","n",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,24,1,"j","n",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,7,11,5,1,"j","n",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,7,11,14,1,"j","n",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,7,11,22,1,"j","n",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,1,12,4,1,"j","j",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,1,12,15,1,"j","j",9.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,1,12,18,{"$f":"IF(AND(B1047>$D$13,B1047<$I$13),0,IF(B1047=$D$13,IF(D1047>=$D$12,0,1),IF(B1047=$I$13,IF(D1047<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C1047=7),AND($I$9=1,C1047>5)),\"n\",IF($I$9=2,G1047,\"j\"))","v":"j"},9.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,1,12,24,1,"j","j",6.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,2,13,8,1,"j","j",3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,2,13,17,1,"j","j",3.3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,3,14,1,1,"j","j",0.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,3,14,10,1,"j","j",0.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,3,14,15,1,"j","j",3.2,null,null,17,null,null,{"$f":"IF(($L1092-$I1092)/(($C$4-$C$16))>=O$21,1*$F1092,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,4,15,3,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,15,5,1,"j","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,15,12,1,"j","j",2.2999999999999998,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,15,21,1,"j","j",1.1000000000000001,null,null,16,null,null,{"$f":"IF(($L1122-$I1122)/(($C$4-$C$16))>=O$21,1*$F1122,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,5,16,4,1,"j","j",7.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,16,14,1,"j","j",9.8000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,6,17,1,1,"j","n",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,6,17,7,1,"j","n",4.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,17,15,1,"j","n",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,6,17,24,1,"j","n",2.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,18,1,1,"j","n",2.4,null,null,{"$f":"IF(AND(H1174=\"j\",OR(AND($C$9<=E1174,E1174<$C$10),AND($D$9<=E1174,E1174<$D$10))),$J$5,$C$5)*F1174","v":16},null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,18,9,1,"j","n",2.5,null,null,16,null,null,{"$f":"IF(($L1182-$I1182)/(($C$4-$C$16))>=O$21,1*$F1182,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,7,18,22,1,"j","n",6.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,19,2,1,"j","j",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,19,12,1,"j","j",6.3,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,19,19,1,"j","j",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,2,20,2,1,"j","j",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,20,12,1,"j","j",7.3,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,2,20,13,1,"j","j",8.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,21,1,1,"j","j",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,3,21,6,1,"j","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,3,21,18,1,"j","j",7.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,21,23,1,"j","j",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,22,8,1,"j","j",-1.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,22,16,1,"j","j",1.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,22,22,1,"j","j",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,5,23,1,1,"j","j",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,5,23,12,1,"j","j",-1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,5,23,18,1,"j","j",0.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,24,2,1,"j","n",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,6,24,11,1,"j","n",-3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,2,6,24,19,1,"j","n",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,25,4,1,"j","n",-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,7,25,13,1,"j","n",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,7,25,18,1,"j","n",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,7,25,22,1,"j","n",-4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,2,1,26,8,1,"n","j",-4.5,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,2,1,26,15,1,"n","j",-1.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,1,26,22,1,"n","j",-2.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,27,8,1,"n","j",-4.0999999999999996,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,2,2,27,12,1,"n","j",-0.9,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,28,1,1,"n","j",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,28,2,1,"n","j",-2.1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,28,10,1,"n","j",-1.6,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,28,19,1,"n","j",0.7,null,null,16,null,null,{"$f":"IF(($L1432-$I1432)/(($C$4-$C$16))>=O$21,1*$F1432,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,3,4,1,3,1,"n","j",-4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,3,4,1,9,1,"n","j",-5.7,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,3,4,1,20,1,"n","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,5,2,5,1,"n","j",-5.4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,3,5,2,8,1,"n","j",-6.7,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,3,5,2,14,1,"n","j",4.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,5,2,22,1,"n","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,6,3,7,1,"n","n",-3.7,null,null,16,null,null,{"$f":"IF(($L1492-$I1492)/(($C$4-$C$16))>=O$21,1*$F1492,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,3,6,3,19,1,"n","n",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,6,3,24,1,"n","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,7,4,5,1,"n","n",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,7,4,17,1,"n","n",10.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,7,4,19,1,"n","n",6.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,1,5,2,1,"j","j",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,1,5,16,1,"j","j",11.5,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,1,5,19,1,"j","j",8.5,null,null,16,null,null,{"$f":"IF(($L1552-$I1552)/(($C$4-$C$16))>=O$21,1*$F1552,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,3,2,6,6,1,"j","j",6.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,2,6,12,1,"j","j",9.8000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,2,6,21,1,"j","j",9.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,3,7,5,1,"j","j",7.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,3,7,14,1,"j","j",11.3,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,3,7,19,1,"j","j",10.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,3,7,23,1,"j","j",8.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,4,8,12,1,"j","j",11.9,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,3,4,8,16,1,"j","j",13.8,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,3,5,9,2,1,"j","j",8.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,5,9,9,1,"j","j",7.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,5,9,16,1,"j","j",11.1,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,6,10,2,1,"j","n",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,6,10,6,1,"j","n",6.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,6,10,11,1,"j","n",8.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,6,10,23,1,"j","n",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,7,11,4,1,"j","n",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,7,11,13,1,"j","n",8.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,7,11,19,1,"j","n",9.6999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,1,12,6,1,"j","j",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,1,12,12,1,"j","j",4.9000000000000004,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,1,12,15,1,"j","j",4.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,2,13,2,1,"j","j",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,2,13,8,1,"j","j",3.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,2,13,16,1,"j","j",7.9,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,3,14,1,1,"j","j",6.7,null,null,{"$f":"IF(AND(H1750=\"j\",OR(AND($C$9<=E1750,E1750<$C$10),AND($D$9<=E1750,E1750<$D$10))),$J$5,$C$5)*F1750","v":16},null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,3,14,6,1,"j","j",8.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,3,14,18,1,"j","j",13.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,3,3,14,23,1,"j","j",8.4,null,null,16,null,null,{"$f":"IF(($L1772-$I1772)/(($C$4-$C$16))>=O$21,1*$F1772,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,3,4,15,3,1,"j","j",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,4,15,13,1,"j","j",12.9,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,3,4,15,20,1,"j","j",10.199999999999999,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,5,16,5,1,"j","j",7.2,null,null,16,null,null,{"$f":"IF(($L1802-$I1802)/(($C$4-$C$16))>=O$21,1*$F1802,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,3,5,16,12,1,"j","j",9.1,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,5,16,22,1,"j","j",6.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,6,17,2,1,"j","n",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,6,17,15,1,"j","n",12.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,3,6,17,16,1,"j","n",12.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,3,6,17,24,1,"j","n",8.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,7,18,13,1,"j","n",12.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,3,7,18,17,1,"j","n",11.7,null,null,16,null,null,{"$f":"IF(($L1862-$I1862)/(($C$4-$C$16))>=O$21,1*$F1862,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,3,7,18,23,1,"j","n",8.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,1,19,10,{"$f":"IF(AND(B1879>$D$13,B1879<$I$13),0,IF(B1879=$D$13,IF(D1879>=$D$12,0,1),IF(B1879=$I$13,IF(D1879<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C1879=7),AND($I$9=1,C1879>5)),\"n\",IF($I$9=2,G1879,\"j\"))","v":"j"},6.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,1,19,13,1,"j","j",8.3000000000000007,null,null,17,null,null,{"$f":"IF(($L1882-$I1882)/(($C$4-$C$16))>=O$21,1*$F1882,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,3,2,20,3,1,"j","j",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,2,20,10,1,"j","j",4.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,2,20,12,1,"j","j",7.8,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,2,20,21,1,"j","j",6.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,3,21,9,1,"j","j",2.1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,3,21,14,1,"j","j",3.3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,3,21,23,1,"j","j",1.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,4,22,7,1,"j","j",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,4,22,13,1,"j","j",0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,4,22,16,1,"j","j",1.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,5,23,6,1,"j","j",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,5,23,9,1,"j","j",-0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,5,23,20,1,"j","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,6,24,2,1,"j","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,6,24,10,1,"j","n",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,6,24,19,1,"j","n",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,6,24,24,1,"j","n",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,7,25,4,1,"j","n",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,7,25,13,1,"j","n",6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,7,25,23,1,"j","n",7.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,1,26,6,1,"j","j",6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,1,26,13,1,"j","j",5.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,1,26,23,1,"j","j",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,2,27,6,1,"j","j",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,2,27,16,1,"j","j",9.9,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,2,27,20,1,"j","j",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,3,28,1,1,"j","j",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,3,28,10,1,"j","j",7.1,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,3,28,18,1,"j","j",10.3,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,3,28,24,1,"j","j",6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,4,29,11,1,"j","j",8.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,4,29,17,1,"j","j",7.2,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,5,30,4,1,"j","j",4.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,5,30,5,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,5,30,13,1,"j","j",8.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,5,30,22,1,"j","j",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,6,31,6,1,"j","n",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,6,31,15,1,"j","n",4.2,null,null,16,null,null,{"$f":"IF(($L2172-$I2172)/(($C$4-$C$16))>=O$21,1*$F2172,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,3,6,31,20,1,"j","n",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,7,1,8,1,"j","n",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,7,1,10,1,"j","n",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,7,1,17,1,"j","n",8.8000000000000007,null,null,{"$f":"IF(AND(H2198=\"j\",OR(AND($C$9<=E2198,E2198<$C$10),AND($D$9<=E2198,E2198<$D$10))),$J$5,$C$5)*F2198","v":16},null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,1,2,7,1,"n","j",4.8,null,null,16,null,null,{"$f":"IF(($L2212-$I2212)/(($C$4-$C$16))>=O$21,1*$F2212,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,4,1,2,10,1,"n","j",7,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,1,2,17,1,"n","j",8.6999999999999993,null,null,17,null,null,{"$f":"IF(($L2222-$I2222)/(($C$4-$C$16))>=O$21,1*$F2222,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,4,2,3,3,1,"n","j",7.7,null,null,16,null,null,{"$f":"IF(($L2232-$I2232)/(($C$4-$C$16))>=O$21,1*$F2232,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,4,2,3,7,1,"n","j",7.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,2,3,20,1,"n","j",7.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,3,4,5,1,"n","j",6.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,3,4,6,1,"n","j",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,3,4,14,1,"n","j",7.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,4,5,3,1,"n","j",6.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,4,5,7,1,"n","j",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,4,5,17,1,"n","j",5.0999999999999996,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,4,5,24,1,"n","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,5,6,7,1,"n","j",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,5,6,17,1,"n","j",6.1,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,5,6,24,1,"n","j",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,6,7,2,{"$f":"IF(AND(B2327>$D$13,B2327<$I$13),0,IF(B2327=$D$13,IF(D2327>=$D$12,0,1),IF(B2327=$I$13,IF(D2327<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C2327=7),AND($I$9=1,C2327>5)),\"n\",IF($I$9=2,G2327,\"j\"))","v":"n"},4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,6,7,14,1,"n","n",7.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,6,7,19,1,"n","n",10.199999999999999,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,7,8,4,1,"n","n",9.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,7,8,12,1,"n","n",8.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,7,8,21,1,"n","n",8.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,1,9,3,1,"n","j",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,1,9,6,1,"n","j",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,1,9,17,1,"n","j",7.8,null,null,{"$f":"IF(AND(H2390=\"j\",OR(AND($C$9<=E2390,E2390<$C$10),AND($D$9<=E2390,E2390<$D$10))),$J$5,$C$5)*F2390","v":17},null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,1,9,23,1,"n","j",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,2,10,7,1,"n","j",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,2,10,16,1,"n","j",10.6,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,2,10,24,1,"n","j",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,3,11,9,1,"n","j",7.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,3,11,14,1,"n","j",10.8,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,3,11,18,1,"n","j",10.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,4,12,4,1,"n","j",8.6999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,4,12,11,1,"n","j",9.6,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,4,12,18,1,"n","j",10.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,4,5,13,4,1,"n","j",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,5,13,13,1,"n","j",8,null,null,17,null,null,{"$f":"IF(($L2482-$I2482)/(($C$4-$C$16))>=O$21,1*$F2482,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,4,5,13,17,1,"n","j",8.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,6,14,6,1,"n","n",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,6,14,7,1,"n","n",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,6,14,15,1,"n","n",9.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,6,14,24,1,"n","n",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,7,15,8,1,"n","n",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,7,15,14,1,"n","n",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,1,16,1,1,"j","j",6.5,null,null,16,null,null,{"$f":"IF(($L2542-$I2542)/(($C$4-$C$16))>=O$21,1*$F2542,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,4,1,16,4,1,"j","j",6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,1,16,18,1,"j","j",6.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,2,17,1,1,"j","j",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,2,17,3,1,"j","j",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,2,17,11,1,"j","j",9.3000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,2,17,20,1,"j","j",11.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,4,3,18,1,1,"j","j",8.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,3,18,13,1,"j","j",16.3,null,null,17,null,null,{"$f":"IF(($L2602-$I2602)/(($C$4-$C$16))>=O$21,1*$F2602,0)","v":0},0,0,0,0,0,0,0,0,0,1]
[null,4,3,18,22,1,"j","j",14.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,4,3,18,24,1,"j","j",11,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,4,4,19,7,1,"j","j",9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,4,19,21,1,"j","j",12.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,4,4,19,24,1,"j","j",9.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,5,20,11,1,"j","j",14.4,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,4,5,20,17,1,"j","j",17.399999999999999,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,4,6,21,1,1,"j","n",9.1999999999999993,null,null,16,null,null,{"$f":"IF(($L2662-$I2662)/(($C$4-$C$16))>=O$21,1*$F2662,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,4,6,21,10,1,"j","n",15.5,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,4,6,21,18,1,"j","n",21.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,4,6,21,19,1,"j","n",20.399999999999999,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,4,7,22,8,1,"j","n",10.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,4,7,22,12,1,"j","n",13.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,4,7,22,22,1,"j","n",11.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,4,1,23,5,1,"j","j",8.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,1,23,14,1,"j","j",15.8,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,4,1,23,21,1,"j","j",14.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,4,2,24,7,1,"j","j",9.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,2,24,11,1,"j","j",18.600000000000001,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,4,2,24,16,1,"j","j",22.9,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,4,3,25,4,1,"j","j",6.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,3,25,9,1,"j","j",7.2,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,3,25,18,{"$f":"IF(AND(B2775>$D$13,B2775<$I$13),0,IF(B2775=$D$13,IF(D2775>=$D$12,0,1),IF(B2775=$I$13,IF(D2775<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C2775=7),AND($I$9=1,C2775>5)),\"n\",IF($I$9=2,G2775,\"j\"))","v":"j"},17.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,4,4,26,2,1,"j","j",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,4,26,8,1,"j","j",7.2,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,4,26,19,1,"j","j",17.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,4,4,26,22,1,"j","j",11.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,4,5,27,4,1,"j","j",6.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,5,27,12,1,"j","j",9.1999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,5,27,21,1,"j","j",8.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,6,28,6,1,"j","n",6.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,6,28,11,1,"j","n",7.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,6,28,23,1,"j","n",6.8,null,null,16,null,null,{"$f":"IF(($L2852-$I2852)/(($C$4-$C$16))>=O$21,1*$F2852,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,4,7,29,4,1,"j","n",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,7,29,8,1,"j","n",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,7,29,18,1,"j","n",7.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,1,30,1,1,"j","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,1,30,8,1,"j","j",4.9000000000000004,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,1,30,18,1,"j","j",10.3,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,1,30,22,1,"j","j",6.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,2,1,11,1,"j","j",9.8000000000000007,null,null,17,null,null,{"$f":"IF(($L2912-$I2912)/(($C$4-$C$16))>=O$21,1*$F2912,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,5,2,1,19,1,"j","j",11,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,2,1,20,1,"j","j",10.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,3,2,5,1,"j","j",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,3,2,13,1,"j","j",14.6,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,3,2,22,1,"j","j",10.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,4,3,4,1,"j","j",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,4,3,15,1,"j","j",13.8,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,4,3,18,{"$f":"IF(AND(B2967>$D$13,B2967<$I$13),0,IF(B2967=$D$13,IF(D2967>=$D$12,0,1),IF(B2967=$I$13,IF(D2967<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C2967=7),AND($I$9=1,C2967>5)),\"n\",IF($I$9=2,G2967,\"j\"))","v":"j"},15.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,5,4,8,1,"j","j",12.2,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,5,4,15,1,"j","j",15.6,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,5,4,17,1,"j","j",17,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,6,5,5,1,"j","n",11.8,null,null,16,null,null,{"$f":"IF(($L3002-$I3002)/(($C$4-$C$16))>=O$21,1*$F3002,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,5,6,5,10,1,"j","n",12,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,6,5,15,1,"j","n",13.1,null,null,16,null,null,{"$f":"IF(($L3012-$I3012)/(($C$4-$C$16))>=O$21,1*$F3012,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,5,7,6,3,1,"j","n",7.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,7,6,12,1,"j","n",11.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,7,6,20,1,"j","n",9.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,1,7,2,1,"j","j",6.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,1,7,5,1,"j","j",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,1,7,14,1,"j","j",9.9,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,2,8,1,1,"j","j",7.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,2,8,7,1,"j","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,2,8,15,1,"j","j",12.5,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,2,8,24,1,"j","j",8.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,3,9,5,1,"j","j",9.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,3,9,9,1,"j","j",11.5,null,null,17,null,null,{"$f":"IF(($L3102-$I3102)/(($C$4-$C$16))>=O$21,1*$F3102,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,5,3,9,22,1,"j","j",13.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,4,10,2,1,"j","j",11.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,4,10,12,1,"j","j",11.1,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,4,10,19,1,"j","j",12,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,5,11,2,1,"j","j",12.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,5,11,12,1,"j","j",12,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,5,11,16,1,"j","j",10.7,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,5,11,21,1,"j","j",8.8000000000000007,null,null,16,null,null,{"$f":"IF(($L3162-$I3162)/(($C$4-$C$16))>=O$21,1*$F3162,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,5,6,12,6,1,"j","n",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,6,12,15,1,"j","n",11,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,6,12,23,1,"j","n",6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,7,13,5,1,"j","n",6.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,7,13,16,1,"j","n",13.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,7,13,22,1,"j","n",12.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,1,14,9,1,"j","j",11.7,null,null,{"$f":"IF(AND(H3222=\"j\",OR(AND($C$9<=E3222,E3222<$C$10),AND($D$9<=E3222,E3222<$D$10))),$J$5,$C$5)*F3222","v":17},null,null,{"$f":"IF(($L3222-$I3222)/(($C$4-$C$16))>=O$21,1*$F3222,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,5,1,14,12,1,"j","j",13.9,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,1,14,18,1,"j","j",15.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,2,15,2,0,"j","j",8.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,15,11,0,"j","j",12.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,15,16,0,"j","j",15.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,16,4,0,"j","j",11.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,16,9,0,"j","j",12.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,16,21,0,"j","j",9.3000000000000007,null,null,0,null,null,{"$f":"IF(($L3282-$I3282)/(($C$4-$C$16))>=O$21,1*$F3282,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,5,3,16,22,0,"j","j",8.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,17,12,0,"j","j",8.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,17,15,0,"j","j",9.8000000000000007,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,17,22,0,"j","j",6.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,5,18,8,0,"j","j",6.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,5,18,12,0,"j","j",10.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,19,1,0,"j","n",6.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,19,9,0,"j","n",8.5,null,null,0,null,null,{"$f":"IF(($L3342-$I3342)/(($C$4-$C$16))>=O$21,1*$F3342,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,5,6,19,10,0,"j","n",10,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,19,23,0,"j","n",5.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,7,20,3,0,"j","n",3.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,7,20,9,0,"j","n",7.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,7,20,20,0,"j","n",9.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,1,21,6,0,"j","j",6.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,1,21,13,0,"j","j",11.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,1,21,22,0,"j","j",9.6999999999999993,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,22,5,0,"j","j",8.1999999999999993,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,22,7,0,"j","j",8.3000000000000007,null,null,0,null,null,{"$f":"IF(($L3412-$I3412)/(($C$4-$C$16))>=O$21,1*$F3412,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,5,2,22,19,0,"j","j",12.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,22,24,0,"j","j",10.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,23,9,0,"j","j",9.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,23,17,0,"j","j",14.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,23,23,0,"j","j",11.9,null,null,0,null,null,{"$f":"IF(($L3452-$I3452)/(($C$4-$C$16))>=O$21,1*$F3452,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,5,4,24,10,0,"j","j",14.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,24,16,0,"j","j",19.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,24,19,0,"j","j",19.2,null,null,0,null,null,{"$f":"IF(($L3472-$I3472)/(($C$4-$C$16))>=O$21,1*$F3472,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,5,5,25,6,0,"j","j",8.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,5,25,12,0,"j","j",18.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,5,25,20,0,"j","j",17.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,26,5,0,"j","n",11.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,26,14,0,"j","n",17,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,26,19,0,"j","n",17.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,26,23,0,"j","n",13.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,7,27,9,0,"j","n",12.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,7,27,16,0,"j","n",19.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,7,27,23,0,"j","n",15,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,1,28,9,0,"j","j",12.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,1,28,16,0,"j","j",19.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,29,2,0,"j","j",11.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,29,6,0,"j","j",10.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,29,11,0,"j","j",12.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,29,20,0,"j","j",17.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,30,4,0,"j","j",13.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,30,10,{"$f":"IF(AND(B3607>$D$13,B3607<$I$13),0,IF(B3607=$D$13,IF(D3607>=$D$12,0,1),IF(B3607=$I$13,IF(D3607<$I$12,0,1),1)))","v":0},"j",{"$f":"IF(OR(AND($I$9=3,C3607=7),AND($I$9=1,C3607>5)),\"n\",IF($I$9=2,G3607,\"j\"))","v":"j"},13.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,30,21,0,"j","j",17.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,31,6,0,"j","j",7.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,31,9,0,"j","j",13.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,31,23,0,"j","j",16.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,1,6,0,"j","j",14.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,1,8,0,"j","j",14.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,1,16,0,"j","j",19.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,2,1,0,"j","n",15.5,null,null,{"$f":"IF(AND(H3670=\"j\",OR(AND($C$9<=E3670,E3670<$C$10),AND($D$9<=E3670,E3670<$D$10))),$J$5,$C$5)*F3670","v":0},null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,2,6,0,"j","n",14.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,2,18,0,"j","n",20,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,3,3,0,"j","n",13.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,3,11,0,"j","n",13.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,3,17,0,"j","n",18,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,3,20,0,"j","n",18.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,4,3,0,"j","j",11.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,4,13,0,"j","j",23.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,4,22,0,"j","j",20.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,5,6,0,"j","j",16.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,5,15,0,"j","j",16.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,5,23,0,"j","j",12.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,5,24,0,"j","j",11.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,6,13,0,"j","j",21.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,6,17,0,"j","j",23.7,null,null,0,null,null,{"$f":"IF(($L3782-$I3782)/(($C$4-$C$16))>=O$21,1*$F3782,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,4,7,3,0,"j","j",16.8,null,null,0,null,null,{"$f":"IF(($L3792-$I3792)/(($C$4-$C$16))>=O$21,1*$F3792,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,4,7,10,{"$f":"IF(AND(B3799>$D$13,B3799<$I$13),0,IF(B3799=$D$13,IF(D3799>=$D$12,0,1),IF(B3799=$I$13,IF(D3799<$I$12,0,1),1)))","v":0},"j",{"$f":"IF(OR(AND($I$9=3,C3799=7),AND($I$9=1,C3799>5)),\"n\",IF($I$9=2,G3799,\"j\"))","v":"j"},16.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,7,17,0,"j","j",17.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,8,3,0,"j","j",13.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,8,10,0,"j","j",15.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,8,12,0,"j","j",17.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,8,24,0,"j","j",13.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,9,5,0,"j","n",10.5,null,null,0,null,null,{"$f":"IF(($L3842-$I3842)/(($C$4-$C$16))>=O$21,1*$F3842,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,6,9,14,0,"j","n",20.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,9,23,0,"j","n",16,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,10,7,0,"j","n",15.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,10,13,0,"j","n",23.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,10,24,0,"j","n",18.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,11,3,0,"j","j",15.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,11,9,0,"j","j",16.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,11,17,0,"j","j",21.8,null,null,0,null,null,{"$f":"IF(($L3902-$I3902)/(($C$4-$C$16))>=O$21,1*$F3902,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,2,12,2,0,"j","j",13.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,12,10,0,"j","j",17.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,12,19,0,"j","j",27,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,12,24,0,"j","j",21.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,13,12,0,"j","j",27.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,13,14,0,"j","j",28.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,13,21,0,"j","j",18.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,14,6,0,"j","j",12.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,14,13,0,"j","j",18.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,14,23,0,"j","j",14,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,15,3,0,"j","j",12.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,15,16,0,"j","j",17.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,15,24,0,"j","j",12.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,16,1,0,"j","n",11.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,16,10,0,"j","n",15.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,16,18,0,"j","n",18.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,16,24,0,"j","n",11.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,17,11,0,"j","n",17,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,17,21,0,"j","n",18.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,18,4,0,"j","j",14.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,18,11,0,"j","j",18.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,18,13,0,"j","j",21.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,18,21,0,"j","j",16.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,19,6,0,"j","j",13.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,19,15,0,"j","j",13.6,null,null,0,null,null,{"$f":"IF(($L4092-$I4092)/(($C$4-$C$16))>=O$21,1*$F4092,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,2,19,20,0,"j","j",12.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,20,8,0,"j","j",10.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,20,17,0,"j","j",13.1,null,null,{"$f":"IF(AND(H4118=\"j\",OR(AND($C$9<=E4118,E4118<$C$10),AND($D$9<=E4118,E4118<$D$10))),$J$5,$C$5)*F4118","v":0},null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,21,1,0,"j","j",6.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,21,7,0,"j","j",8.1999999999999993,null,null,0,null,null,{"$f":"IF(($L4132-$I4132)/(($C$4-$C$16))>=O$21,1*$F4132,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,4,21,10,0,"j","j",12.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,21,21,0,"j","j",10.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,22,3,0,"j","j",8.9,null,null,0,null,null,{"$f":"IF(($L4152-$I4152)/(($C$4-$C$16))>=O$21,1*$F4152,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,5,22,11,0,"j","j",12.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,22,20,0,"j","j",11.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,23,4,0,"j","n",7.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,23,13,0,"j","n",15.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,23,18,0,"j","n",15.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,23,22,0,"j","n",12.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,24,7,0,"j","n",7.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,24,17,0,"j","n",18.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,24,24,0,"j","n",13.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,25,7,0,"j","j",9.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,25,17,0,"j","j",22,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,25,21,0,"j","j",19.3,null,null,0,null,null,{"$f":"IF(($L4242-$I4242)/(($C$4-$C$16))>=O$21,1*$F4242,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,2,26,2,{"$f":"IF(AND(B4247>$D$13,B4247<$I$13),0,IF(B4247=$D$13,IF(D4247>=$D$12,0,1),IF(B4247=$I$13,IF(D4247<$I$12,0,1),1)))","v":0},"j",{"$f":"IF(OR(AND($I$9=3,C4247=7),AND($I$9=1,C4247>5)),\"n\",IF($I$9=2,G4247,\"j\"))","v":"j"},14.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,26,11,0,"j","j",19.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,26,19,0,"j","j",23.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,27,4,0,"j","j",14.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,27,12,0,"j","j",23.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,27,18,0,"j","j",24.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,28,5,0,"j","j",14.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,28,8,0,"j","j",15.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,28,14,0,"j","j",18.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,28,23,0,"j","j",17.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,29,7,0,"j","j",16.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,29,16,0,"j","j",15.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,29,21,0,"j","j",13.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,30,9,0,"j","n",13.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,30,14,0,"j","n",18.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,1,2,0,"n","n",10.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,1,4,0,"n","n",9.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,1,11,0,"n","n",13.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,1,18,0,"n","n",14.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,2,4,0,"n","j",10.199999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,2,15,0,"n","j",17.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,2,21,0,"n","j",16.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,3,5,0,"n","j",13.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,3,14,0,"n","j",11.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,3,15,0,"n","j",10.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,4,4,0,"n","j",9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,4,8,0,"n","j",11.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,4,14,0,"n","j",14.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,5,1,0,"n","j",9.3000000000000007,null,null,0,null,null,{"$f":"IF(($L4462-$I4462)/(($C$4-$C$16))>=O$21,1*$F4462,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,4,5,11,0,"n","j",12.4,null,null,0,null,null,{"$f":"IF(($L4472-$I4472)/(($C$4-$C$16))>=O$21,1*$F4472,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,4,5,18,0,"n","j",13,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,6,1,0,"n","j",10.199999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,6,3,0,"n","j",9.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,6,15,0,"n","j",13.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,6,20,0,"n","j",13,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,7,8,0,"n","n",13,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,7,13,0,"n","n",18.100000000000001,null,null,0,null,null,{"$f":"IF(($L4522-$I4522)/(($C$4-$C$16))>=O$21,1*$F4522,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,6,7,22,0,"n","n",14.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,8,6,0,"n","n",7.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,8,15,0,"n","n",21.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,8,21,0,"n","n",17.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,8,24,0,"n","n",13.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,9,11,0,"n","j",15.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,9,17,0,"n","j",23.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,10,1,0,"n","j",16.100000000000001,null,null,0,null,null,{"$f":"IF(($L4582-$I4582)/(($C$4-$C$16))>=O$21,1*$F4582,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,2,10,10,0,"n","j",22.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,10,15,0,"n","j",22.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,11,3,0,"n","j",16.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,11,8,0,"n","j",15.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,11,12,0,"n","j",19,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,11,22,0,"n","j",15.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,12,5,0,"n","j",14.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,12,12,0,"n","j",14.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,12,22,0,"n","j",14.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,13,7,0,"n","j",13.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,13,11,0,"n","j",16.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,13,16,0,"n","j",18.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,14,1,0,"n","n",13.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,14,9,0,"n","n",16.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,14,15,0,"n","n",21.4,null,null,0,null,null,{"$f":"IF(($L4692-$I4692)/(($C$4-$C$16))>=O$21,1*$F4692,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,7,15,2,0,"n","n",15.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,15,8,0,"n","n",15.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,15,19,0,"n","n",16.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,15,22,0,"n","n",16.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,16,4,0,"n","j",14.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,16,12,0,"n","j",16.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,16,21,0,"n","j",15,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,17,9,0,"n","j",13.1,null,null,{"$f":"IF(AND(H4758=\"j\",OR(AND($C$9<=E4758,E4758<$C$10),AND($D$9<=E4758,E4758<$D$10))),$J$5,$C$5)*F4758","v":0},null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,17,14,0,"n","j",16.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,17,23,0,"n","j",11.4,null,null,0,null,null,{"$f":"IF(($L4772-$I4772)/(($C$4-$C$16))>=O$21,1*$F4772,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,3,18,8,0,"n","j",11.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,18,16,0,"n","j",19.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,18,22,0,"n","j",15.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,19,1,0,"n","j",12.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,19,8,0,"n","j",15.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,19,18,0,"n","j",18.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,20,5,0,"n","j",15.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,20,11,0,"n","j",19.5,null,null,0,null,null,{"$f":"IF(($L4832-$I4832)/(($C$4-$C$16))>=O$21,1*$F4832,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,5,20,19,0,"n","j",23,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,21,4,0,"n","n",19.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,21,9,0,"n","n",18.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,21,13,0,"n","n",20.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,22,2,0,"n","n",16,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,22,6,0,"n","n",14.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,22,15,0,"n","n",18.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,22,22,0,"n","n",15.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,23,8,0,"n","j",13.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,23,15,0,"n","j",19,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,23,17,0,"n","j",18.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,24,5,0,"n","j",8.6,null,null,0,null,null,{"$f":"IF(($L4922-$I4922)/(($C$4-$C$16))>=O$21,1*$F4922,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,2,24,10,0,"n","j",16,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,24,19,0,"n","j",21.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,25,3,0,"n","j",13.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,25,9,0,"n","j",16.100000000000001,null,null,{"$f":"IF(AND(H4950=\"j\",OR(AND($C$9<=E4950,E4950<$C$10),AND($D$9<=E4950,E4950<$D$10))),$J$5,$C$5)*F4950","v":0},null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,25,20,0,"n","j",22.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,26,2,0,"n","j",19.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,26,5,0,"n","j",18.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,26,16,0,"n","j",21.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,26,22,0,"n","j",17.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,27,7,0,"n","j",14.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,27,15,0,"n","j",14.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,27,24,0,"n","j",12.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,28,5,0,"n","n",10.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,28,17,0,"n","n",16.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,28,19,0,"n","n",15.6,null,null,0,null,null,{"$f":"IF(($L5032-$I5032)/(($C$4-$C$16))>=O$21,1*$F5032,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,7,29,2,0,"n","n",9.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,29,9,0,"n","n",11.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,29,19,0,"n","n",18.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,30,2,0,"n","j",9.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,30,12,0,"n","j",19,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,30,16,0,"n","j",20.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,31,5,0,"n","j",14.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,31,6,0,"n","j",14.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,31,14,0,"n","j",20.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,31,23,0,"n","j",15.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,1,5,0,"n","j",9.8000000000000007,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,1,16,0,"n","j",22.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,2,2,0,"n","j",16,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,2,9,0,"n","j",15.3,null,null,{"$f":"IF(AND(H5142=\"j\",OR(AND($C$9<=E5142,E5142<$C$10),AND($D$9<=E5142,E5142<$D$10))),$J$5,$C$5)*F5142","v":0},null,null,{"$f":"IF(($L5142-$I5142)/(($C$4-$C$16))>=O$21,1*$F5142,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,4,2,16,0,"n","j",18.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,2,18,0,"n","j",18.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,3,2,0,"n","j",12.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,3,11,0,"n","j",16.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,3,23,0,"n","j",15.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,4,4,0,"n","n",15,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,4,13,0,"n","n",19.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,4,21,0,"n","n",18.2,null,null,0,null,null,{"$f":"IF(($L5202-$I5202)/(($C$4-$C$16))>=O$21,1*$F5202,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,7,5,3,0,"n","n",18.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,5,6,0,"n","n",18.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,5,15,0,"n","n",27,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,6,2,0,"n","j",16,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,6,8,0,"n","j",16.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,6,16,0,"n","j",20.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,7,1,0,"n","j",13.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,7,9,0,"n","j",16.8,null,null,0,null,null,{"$f":"IF(($L5262-$I5262)/(($C$4-$C$16))>=O$21,1*$F5262,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,2,7,18,{"$f":"IF(AND(B5271>$D$13,B5271<$I$13),0,IF(B5271=$D$13,IF(D5271>=$D$12,0,1),IF(B5271=$I$13,IF(D5271<$I$12,0,1),1)))","v":0},"n",{"$f":"IF(OR(AND($I$9=3,C5271=7),AND($I$9=1,C5271>5)),\"n\",IF($I$9=2,G5271,\"j\"))","v":"j"},21.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,7,23,0,"n","j",16.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,8,3,0,"n","j",14.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,8,13,0,"n","j",22.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,8,20,0,"n","j",19.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,9,3,0,"n","j",15,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,9,13,0,"n","j",20.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,9,20,0,"n","j",20.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,10,6,0,"n","j",13.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,10,7,0,"n","j",14,null,null,0,null,null,{"$f":"IF(($L5332-$I5332)/(($C$4-$C$16))>=O$21,1*$F5332,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,5,10,16,0,"n","j",21.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,10,24,0,"n","j",16,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,11,9,0,"n","n",16.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,11,17,0,"n","n",20.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,11,23,0,"n","n",14.5,null,null,0,null,null,{"$f":"IF(($L5372-$I5372)/(($C$4-$C$16))>=O$21,1*$F5372,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,7,12,10,0,"n","n",15.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,12,13,0,"n","n",17.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,12,19,0,"n","n",17,null,null,0,null,null,{"$f":"IF(($L5392-$I5392)/(($C$4-$C$16))>=O$21,1*$F5392,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,1,13,3,0,"n","j",7.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,13,12,0,"n","j",17.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,13,20,0,"n","j",16.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,14,5,0,"n","j",11.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,14,10,0,"n","j",15.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,14,22,0,"n","j",13,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,15,7,0,"n","j",13.9,null,null,0,null,null,{"$f":"IF(($L5452-$I5452)/(($C$4-$C$16))>=O$21,1*$F5452,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,3,15,9,0,"n","j",13.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,15,16,0,"n","j",16.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,15,23,0,"n","j",11.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,16,9,0,"n","j",13.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,16,20,0,"n","j",13.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,17,2,0,"n","j",13.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,17,10,0,"n","j",13.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,17,19,0,"n","j",16.3,null,null,0,null,null,{"$f":"IF(($L5512-$I5512)/(($C$4-$C$16))>=O$21,1*$F5512,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,5,17,20,0,"n","j",15.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,18,4,0,"n","n",11.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,18,17,0,"n","n",17,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,18,21,0,"n","n",17.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,19,7,0,"n","n",14.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,19,14,0,"n","n",15.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,19,21,0,"n","n",14,null,null,0,null,null,{"$f":"IF(($L5562-$I5562)/(($C$4-$C$16))>=O$21,1*$F5562,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,1,20,7,0,"n","j",13.2,null,null,0,null,null,{"$f":"IF(($L5572-$I5572)/(($C$4-$C$16))>=O$21,1*$F5572,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,1,20,8,0,"n","j",13.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,20,20,0,"n","j",17.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,21,1,0,"n","j",14.1,null,null,{"$f":"IF(AND(H5590=\"j\",OR(AND($C$9<=E5590,E5590<$C$10),AND($D$9<=E5590,E5590<$D$10))),$J$5,$C$5)*F5590","v":0},null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,21,13,0,"n","j",19.2,null,null,0,null,null,{"$f":"IF(($L5602-$I5602)/(($C$4-$C$16))>=O$21,1*$F5602,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,2,21,18,0,"n","j",19.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,22,3,0,"n","j",14.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,22,11,0,"n","j",15.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,22,17,0,"n","j",16.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,22,20,0,"n","j",15.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,23,7,0,"n","j",12.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,23,13,0,"n","j",17,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,23,21,0,"n","j",15.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,24,6,0,"n","j",12.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,24,14,0,"n","j",15.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,24,23,0,"n","j",16.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,25,8,0,"n","n",16.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,25,13,0,"n","n",19.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,25,17,0,"n","n",20.9,null,null,0,null,null,{"$f":"IF(($L5702-$I5702)/(($C$4-$C$16))>=O$21,1*$F5702,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,7,26,3,0,"n","n",15.3,null,null,0,null,null,{"$f":"IF(($L5712-$I5712)/(($C$4-$C$16))>=O$21,1*$F5712,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,7,26,10,{"$f":"IF(AND(B5719>$D$13,B5719<$I$13),0,IF(B5719=$D$13,IF(D5719>=$D$12,0,1),IF(B5719=$I$13,IF(D5719<$I$12,0,1),1)))","v":0},"n",{"$f":"IF(OR(AND($I$9=3,C5719=7),AND($I$9=1,C5719>5)),\"n\",IF($I$9=2,G5719,\"j\"))","v":"n"},20.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,26,17,0,"n","n",25,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,27,3,0,"n","j",16.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,27,7,0,"n","j",17.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,27,20,0,"n","j",19.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,27,21,0,"n","j",17.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,28,5,0,"n","j",10.199999999999999,null,null,0,null,null,{"$f":"IF(($L5762-$I5762)/(($C$4-$C$16))>=O$21,1*$F5762,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,2,28,14,0,"n","j",24.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,28,22,0,"n","j",17.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,29,4,0,"n","j",13.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,29,15,0,"n","j",28.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,29,24,0,"n","j",20.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,30,3,0,"n","j",20.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,30,9,0,"n","j",22.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,30,17,0,"n","j",27.9,null,null,0,null,null,{"$f":"IF(($L5822-$I5822)/(($C$4-$C$16))>=O$21,1*$F5822,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,5,31,2,0,"n","j",16.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,31,14,0,"n","j",18.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,31,19,0,"n","j",18.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,31,24,0,"n","j",17.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,1,12,0,"j","n",17.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,1,14,0,"j","n",18.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,1,21,0,"j","n",15.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,2,11,0,"j","n",16.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,2,14,0,"j","n",19.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,1,3,1,0,"j","j",16.8,null,null,0,null,null,{"$f":"IF(($L5902-$I5902)/(($C$4-$C$16))>=O$21,1*$F5902,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,9,1,3,7,0,"j","j",16,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,1,3,16,0,"j","j",19.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,1,3,24,0,"j","j",13.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,4,9,0,"j","j",15.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,4,14,0,"j","j",17.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,4,18,0,"j","j",16.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,5,7,0,"j","j",15,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,5,11,0,"j","j",18.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,5,21,0,"j","j",19,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,6,4,0,"j","j",14.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,6,11,0,"j","j",18.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,6,21,0,"j","j",16.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,7,1,0,"j","j",14.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,7,6,0,"j","j",14,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,7,15,0,"j","j",24.4,null,null,0,null,null,{"$f":"IF(($L6012-$I6012)/(($C$4-$C$16))>=O$21,1*$F6012,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,9,5,7,23,0,"j","j",18.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,8,8,0,"j","n",19.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,8,14,0,"j","n",21.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,9,1,0,"j","n",16.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,9,7,0,"j","n",15.9,null,null,0,null,null,{"$f":"IF(($L6052-$I6052)/(($C$4-$C$16))>=O$21,1*$F6052,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,9,7,9,10,0,"j","n",17.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,9,21,0,"j","n",14.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,1,10,3,0,"j","j",14.1,null,null,0,null,null,{"$f":"IF(($L6072-$I6072)/(($C$4-$C$16))>=O$21,1*$F6072,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,9,1,10,11,0,"j","j",15.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,1,10,20,0,"j","j",14.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,11,1,0,"j","j",13.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,11,13,0,"j","j",17.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,11,18,0,"j","j",15.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,11,22,0,"j","j",13.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,12,8,0,"j","j",12.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,12,15,0,"j","j",15,null,null,0,null,null,{"$f":"IF(($L6132-$I6132)/(($C$4-$C$16))>=O$21,1*$F6132,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,9,3,12,24,0,"j","j",13.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,13,7,0,"j","j",10.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,13,17,0,"j","j",15.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,13,21,0,"j","j",12.6,null,null,0,null,null,{"$f":"IF(($L6162-$I6162)/(($C$4-$C$16))>=O$21,1*$F6162,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,9,5,14,10,0,"j","j",15.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,14,11,0,"j","j",15.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,14,19,0,"j","j",17.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,15,8,1,"j","n",16,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,6,15,12,1,"j","n",19.100000000000001,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,15,18,1,"j","n",16.5,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,16,5,1,"j","n",11.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,7,16,8,1,"j","n",10.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,7,16,22,1,"j","n",11.5,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,1,17,5,1,"j","j",12,null,null,16,null,null,{"$f":"IF(($L6242-$I6242)/(($C$4-$C$16))>=O$21,1*$F6242,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,9,1,17,7,1,"j","j",12,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,1,17,16,1,"j","j",18.100000000000001,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,18,4,1,"j","j",9.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,2,18,9,1,"j","j",12.2,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,2,18,18,1,"j","j",21.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,19,2,1,"j","j",13.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,3,19,8,1,"j","j",12.7,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,3,19,11,1,"j","j",19.7,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,20,1,1,"j","j",14.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,4,20,4,1,"j","j",12.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,4,20,15,1,"j","j",21.9,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,20,21,1,"j","j",18.100000000000001,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,21,5,1,"j","j",12.5,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,5,21,14,1,"j","j",21.2,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,21,19,1,"j","j",19.8,null,null,16,null,null,{"$f":"IF(($L6352-$I6352)/(($C$4-$C$16))>=O$21,1*$F6352,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,9,5,21,23,1,"j","j",15.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,6,22,8,1,"j","n",10.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,6,22,18,1,"j","n",17.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,23,1,1,"j","n",8.5,null,null,16,null,null,{"$f":"IF(($L6382-$I6382)/(($C$4-$C$16))>=O$21,1*$F6382,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,9,7,23,8,1,"j","n",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,9,7,23,18,1,"j","n",15.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,1,24,1,1,"j","j",8.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,1,24,11,1,"j","j",11,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,1,24,15,1,"j","j",16.8,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,1,24,20,1,"j","j",14.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,2,25,5,1,"j","j",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,2,25,13,1,"j","j",19.899999999999999,null,null,17,null,null,{"$f":"IF(($L6442-$I6442)/(($C$4-$C$16))>=O$21,1*$F6442,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,9,2,25,19,1,"j","j",19.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,26,6,1,"j","j",11.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,3,26,12,1,"j","j",20.5,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,26,23,1,"j","j",15.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,3,26,24,1,"j","j",15.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,4,27,8,1,"j","j",11.9,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,4,27,17,1,"j","j",23.8,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,28,1,1,"j","j",13.4,null,null,16,null,null,{"$f":"IF(($L6502-$I6502)/(($C$4-$C$16))>=O$21,1*$F6502,0)","v":0},0,0,0,0,0,0,0,0,0,1]
[null,9,5,28,10,1,"j","j",16.2,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,5,28,15,1,"j","j",24.9,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,29,3,1,"j","n",10.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,6,29,5,1,"j","n",8.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,6,29,12,1,"j","n",20.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,30,2,{"$f":"IF(AND(B6551>$D$13,B6551<$I$13),0,IF(B6551=$D$13,IF(D6551>=$D$12,0,1),IF(B6551=$I$13,IF(D6551<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C6551=7),AND($I$9=1,C6551>5)),\"n\",IF($I$9=2,G6551,\"j\"))","v":"n"},15.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,7,30,5,1,"j","n",15.5,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,7,30,12,1,"j","n",12.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,7,30,22,1,"j","n",14,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,1,1,2,1,"j","j",13.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,1,1,15,1,"j","j",16.7,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,1,1,24,1,"j","j",12.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,2,2,1,1,"j","j",12.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,2,2,9,1,"j","j",13.1,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,2,2,22,1,"j","j",12.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,3,3,2,1,"j","j",11,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,3,3,12,1,"j","j",15.5,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,3,3,19,1,"j","j",14.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,4,4,2,1,"j","j",14.5,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,4,4,12,1,"j","j",16,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,4,4,19,1,"j","j",15.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,4,4,21,1,"j","j",14.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,5,5,9,1,"j","j",12.9,null,null,{"$f":"IF(AND(H6678=\"j\",OR(AND($C$9<=E6678,E6678<$C$10),AND($D$9<=E6678,E6678<$D$10))),$J$5,$C$5)*F6678","v":17},null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,5,5,14,1,"j","j",16.7,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,5,5,23,1,"j","j",13.5,null,null,16,null,null,{"$f":"IF(($L6692-$I6692)/(($C$4-$C$16))>=O$21,1*$F6692,0)","v":0},0,0,0,0,0,0,0,0,0,1]
[null,10,6,6,7,1,"j","n",11.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,6,6,16,1,"j","n",15.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,6,6,22,1,"j","n",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,7,7,1,1,"j","n",6.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,7,7,12,1,"j","n",14.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,7,7,18,1,"j","n",13.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,1,8,2,{"$f":"IF(AND(B6743>$D$13,B6743<$I$13),0,IF(B6743=$D$13,IF(D6743>=$D$12,0,1),IF(B6743=$I$13,IF(D6743<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C6743=7),AND($I$9=1,C6743>5)),\"n\",IF($I$9=2,G6743,\"j\"))","v":"j"},11.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,1,8,11,1,"j","j",14.9,null,null,17,null,null,{"$f":"IF(($L6752-$I6752)/(($C$4-$C$16))>=O$21,1*$F6752,0)","v":0},0,0,0,0,0,0,0,0,0,1]
[null,10,1,8,19,1,"j","j",15.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,2,9,4,1,"j","j",14.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,2,9,9,1,"j","j",15.2,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,2,9,13,1,"j","j",16.3,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,2,9,23,1,"j","j",15.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,3,10,6,1,"j","j",14.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,3,10,13,1,"j","j",19.8,null,null,17,null,null,{"$f":"IF(($L6802-$I6802)/(($C$4-$C$16))>=O$21,1*$F6802,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,10,3,10,23,1,"j","j",15.3,null,null,16,null,null,{"$f":"IF(($L6812-$I6812)/(($C$4-$C$16))>=O$21,1*$F6812,0)","v":0},0,0,0,0,0,0,0,0,0,1]
[null,10,4,11,8,1,"j","j",11.4,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,4,11,12,1,"j","j",13.8,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,5,12,1,1,"j","j",11,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,5,12,2,1,"j","j",10.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,5,12,10,1,"j","j",10.8,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,5,12,19,1,"j","j",11.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,6,13,3,1,"j","n",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,6,13,9,1,"j","n",7.5,null,null,{"$f":"IF(AND(H6870=\"j\",OR(AND($C$9<=E6870,E6870<$C$10),AND($D$9<=E6870,E6870<$D$10))),$J$5,$C$5)*F6870","v":16},null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,6,13,20,1,"j","n",11.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,6,13,23,1,"j","n",12.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,7,14,13,1,"j","n",14.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,7,14,20,1,"j","n",12.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,7,14,22,1,"j","n",11.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,1,15,6,1,"j","j",15,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,1,15,15,1,"j","j",14.3,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,1,15,24,1,"j","j",11.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,2,16,5,1,"j","j",11.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,2,16,17,1,"j","j",10.3,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,2,16,19,1,"j","j",9.6999999999999993,null,null,16,null,null,{"$f":"IF(($L6952-$I6952)/(($C$4-$C$16))>=O$21,1*$F6952,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,10,3,17,2,1,"j","j",8.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,3,17,16,1,"j","j",10.5,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,3,17,19,1,"j","j",9.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,4,18,6,1,"j","j",9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,4,18,12,1,"j","j",11.2,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,4,18,20,1,"j","j",8.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,5,19,5,1,"j","j",6.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,5,19,13,1,"j","j",11.4,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,5,19,14,1,"j","j",11.6,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,6,20,3,1,"j","n",11.3,null,null,16,null,null,{"$f":"IF(($L7032-$I7032)/(($C$4-$C$16))>=O$21,1*$F7032,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,10,6,20,7,1,"j","n",11.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,6,20,17,1,"j","n",12.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,6,20,24,1,"j","n",10,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,7,21,9,1,"j","n",12.5,null,null,{"$f":"IF(AND(H7062=\"j\",OR(AND($C$9<=E7062,E7062<$C$10),AND($D$9<=E7062,E7062<$D$10))),$J$5,$C$5)*F7062","v":16},null,null,{"$f":"IF(($L7062-$I7062)/(($C$4-$C$16))>=O$21,1*$F7062,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,10,7,21,16,1,"j","n",12.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,1,22,2,1,"j","j",10.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,1,22,6,1,"j","j",10.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,1,22,11,1,"j","j",12.1,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,1,22,20,1,"j","j",13,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,2,23,4,1,"j","j",12.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,2,23,13,1,"j","j",13.3,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,2,23,21,1,"j","j",10,null,null,16,null,null,{"$f":"IF(($L7122-$I7122)/(($C$4-$C$16))>=O$21,1*$F7122,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,10,3,24,3,1,"j","j",6.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,3,24,14,1,"j","j",9.4,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,3,24,17,1,"j","j",10.3,null,null,17,null,null,{"$f":"IF(($L7142-$I7142)/(($C$4-$C$16))>=O$21,1*$F7142,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,10,3,24,23,1,"j","j",10.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,4,25,7,1,"j","j",10.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,4,25,16,1,"j","j",12.3,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,5,26,1,1,"j","j",10.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,5,26,6,1,"j","j",9.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,5,26,18,{"$f":"IF(AND(B7191>$D$13,B7191<$I$13),0,IF(B7191=$D$13,IF(D7191>=$D$12,0,1),IF(B7191=$I$13,IF(D7191<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C7191=7),AND($I$9=1,C7191>5)),\"n\",IF($I$9=2,G7191,\"j\"))","v":"j"},10.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,5,26,23,1,"j","j",6.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,6,27,3,1,"j","n",4.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,10,6,27,13,1,"j","n",7.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,6,27,20,1,"j","n",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,7,28,3,1,"j","n",6.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,7,28,13,1,"j","n",7.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,7,28,17,1,"j","n",8.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,1,29,6,1,"n","j",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,10,1,29,14,1,"n","j",6.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,1,29,15,1,"n","j",6.8,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,1,29,24,1,"n","j",6.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,2,30,8,1,"n","j",6.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,10,2,30,17,1,"n","j",5.5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,10,2,30,23,1,"n","j",7.6,null,null,16,null,null,{"$f":"IF(($L7292-$I7292)/(($C$4-$C$16))>=O$21,1*$F7292,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,10,3,31,10,1,"n","j",7.9,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,3,31,13,1,"n","j",8.1999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,4,1,3,1,"n","j",8.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,4,1,10,1,"n","j",7.8,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,4,1,12,1,"n","j",12.6,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,11,4,1,24,1,"n","j",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,5,2,5,1,"n","j",6.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,5,2,10,1,"n","j",6.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,5,2,22,1,"n","j",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,6,3,7,1,"n","n",6,null,null,16,null,null,{"$f":"IF(($L7372-$I7372)/(($C$4-$C$16))>=O$21,1*$F7372,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,11,6,3,15,1,"n","n",8.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,6,3,21,1,"n","n",7.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,6,3,24,1,"n","n",7.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,7,4,9,1,"n","n",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,7,4,20,1,"n","n",10.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,11,1,5,2,1,"j","j",10.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,1,5,10,1,"j","j",9.6,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,1,5,19,1,"j","j",9.9,null,null,16,null,null,{"$f":"IF(($L7432-$I7432)/(($C$4-$C$16))>=O$21,1*$F7432,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,11,1,5,24,1,"j","j",9.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,2,6,4,1,"j","j",9.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,2,6,17,1,"j","j",12.8,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,11,2,6,21,1,"j","j",12.5,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,11,3,7,7,1,"j","j",11.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,11,3,7,14,1,"j","j",12.2,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,11,3,7,21,1,"j","j",11.5,null,null,16,null,null,{"$f":"IF(($L7482-$I7482)/(($C$4-$C$16))>=O$21,1*$F7482,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,11,4,8,7,1,"j","j",11.3,null,null,16,null,null,{"$f":"IF(($L7492-$I7492)/(($C$4-$C$16))>=O$21,1*$F7492,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,11,4,8,11,1,"j","j",11.7,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,11,4,8,16,1,"j","j",10,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,5,9,1,1,"j","j",9.1,null,null,{"$f":"IF(AND(H7510=\"j\",OR(AND($C$9<=E7510,E7510<$C$10),AND($D$9<=E7510,E7510<$D$10))),$J$5,$C$5)*F7510","v":16},null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,5,9,10,1,"j","j",8.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,5,9,18,1,"j","j",10,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,5,9,24,1,"j","j",10.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,11,6,10,11,1,"j","n",11.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,11,6,10,17,1,"j","n",10.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,11,7,11,4,1,"j","n",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,7,11,7,1,"j","n",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,7,11,13,1,"j","n",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,7,11,21,1,"j","n",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,1,12,6,1,"j","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,1,12,11,1,"j","j",5.6,null,null,17,null,null,{"$f":"IF(($L7592-$I7592)/(($C$4-$C$16))>=O$21,1*$F7592,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,11,1,12,23,1,"j","j",7.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,2,13,4,1,"j","j",11.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,11,2,13,16,1,"j","j",8.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,2,13,17,1,"j","j",8.3000000000000007,null,null,17,null,null,{"$f":"IF(($L7622-$I7622)/(($C$4-$C$16))>=O$21,1*$F7622,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,11,3,14,7,1,"j","j",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,3,14,10,{"$f":"IF(AND(B7639>$D$13,B7639<$I$13),0,IF(B7639=$D$13,IF(D7639>=$D$12,0,1),IF(B7639=$I$13,IF(D7639<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C7639=7),AND($I$9=1,C7639>5)),\"n\",IF($I$9=2,G7639,\"j\"))","v":"j"},3.7,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,3,14,17,1,"j","j",6.9,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,4,15,3,1,"j","j",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,4,15,7,1,"j","j",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,4,15,20,1,"j","j",2.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,5,16,4,1,"j","j",2.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,5,16,5,1,"j","j",2.7,null,null,16,null,null,{"$f":"IF(($L7682-$I7682)/(($C$4-$C$16))>=O$21,1*$F7682,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,11,5,16,18,1,"j","j",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,5,16,22,1,"j","j",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,6,17,4,1,"j","n",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,6,17,15,1,"j","n",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,7,18,1,1,"j","n",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,7,18,8,1,"j","n",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,7,18,17,1,"j","n",5.6,null,null,16,null,null,{"$f":"IF(($L7742-$I7742)/(($C$4-$C$16))>=O$21,1*$F7742,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,11,7,18,24,1,"j","n",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,1,19,2,1,"j","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,1,19,14,1,"j","j",4.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,1,19,19,1,"j","j",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,2,20,4,1,"j","j",8.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,2,20,12,1,"j","j",8.1999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,2,20,18,1,"j","j",9.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,3,21,5,1,"j","j",6.6,null,null,16,null,null,{"$f":"IF(($L7802-$I7802)/(($C$4-$C$16))>=O$21,1*$F7802,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,11,3,21,11,1,"j","j",6.9,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,3,21,14,1,"j","j",7.8,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,4,22,1,1,"j","j",5.7,null,null,16,null,null,{"$f":"IF(($L7822-$I7822)/(($C$4-$C$16))>=O$21,1*$F7822,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,11,4,22,7,1,"j","j",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,4,22,15,1,"j","j",8.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,4,22,24,1,"j","j",6.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,5,23,9,1,"j","j",4.9000000000000004,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,5,23,14,1,"j","j",7.2,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,5,23,18,1,"j","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,6,24,4,1,"j","n",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,6,24,11,1,"j","n",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,6,24,18,1,"j","n",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,7,25,4,1,"j","n",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,7,25,11,1,"j","n",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,7,25,21,1,"j","n",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,1,26,1,1,"j","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,1,26,6,1,"j","j",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,1,26,15,1,"j","j",4.8,null,null,17,null,null,{"$f":"IF(($L7932-$I7932)/(($C$4-$C$16))>=O$21,1*$F7932,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,11,1,26,23,1,"j","j",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,2,27,5,1,"j","j",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,2,27,16,1,"j","j",5.0999999999999996,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,3,28,1,1,"j","j",2.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,3,28,4,1,"j","j",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,3,28,18,1,"j","j",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,4,29,1,1,"j","j",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,4,29,3,1,"j","j",4.4000000000000004,null,null,16,null,null,{"$f":"IF(($L7992-$I7992)/(($C$4-$C$16))>=O$21,1*$F7992,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,11,4,29,11,1,"j","j",4.5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,4,29,20,1,"j","j",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,5,30,1,1,"j","j",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,5,30,13,1,"j","j",7.8,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,5,30,22,1,"j","j",7.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,1,6,1,"j","n",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,1,12,1,"j","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,1,15,1,"j","n",2.2000000000000002,null,null,16,null,null,{"$f":"IF(($L8052-$I8052)/(($C$4-$C$16))>=O$21,1*$F8052,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,6,1,22,1,"j","n",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,2,8,1,"j","n",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,2,17,1,"j","n",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,1,3,1,1,"j","j",2.8,null,null,{"$f":"IF(AND(H8086=\"j\",OR(AND($C$9<=E8086,E8086<$C$10),AND($D$9<=E8086,E8086<$D$10))),$J$5,$C$5)*F8086","v":16},null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,3,10,1,"j","j",0.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,3,18,1,"j","j",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,3,19,1,"j","j",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,4,8,1,"j","j",3.1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,2,4,12,1,"j","j",5.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,2,4,22,1,"j","j",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,5,5,1,"j","j",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,5,12,1,"j","j",6.7,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,3,5,22,1,"j","j",8.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,4,6,5,1,"j","j",7.7,null,null,16,null,null,{"$f":"IF(($L8162-$I8162)/(($C$4-$C$16))>=O$21,1*$F8162,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,12,4,6,7,1,"j","j",7.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,4,6,19,1,"j","j",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,6,24,1,"j","j",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,7,9,1,"j","j",1.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,7,18,1,"j","j",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,8,2,1,"j","n",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,8,8,1,"j","n",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,6,8,19,1,"j","n",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,6,8,22,1,"j","n",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,9,4,1,"j","n",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,9,12,1,"j","n",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,9,21,1,"j","n",-1.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,10,5,1,"j","j",-2.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,10,14,1,"j","j",-0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,10,19,1,"j","j",-0.8,null,null,16,null,null,{"$f":"IF(($L8272-$I8272)/(($C$4-$C$16))>=O$21,1*$F8272,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,12,2,11,7,1,"j","j",-6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,12,2,11,9,1,"j","j",-5.7,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,12,2,11,16,1,"j","j",-2.1,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,12,3,12,1,1,"j","j",-1.8,null,null,16,null,null,{"$f":"IF(($L8302-$I8302)/(($C$4-$C$16))>=O$21,1*$F8302,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,12,3,12,8,1,"j","j",-1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,12,18,1,"j","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,3,12,22,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,13,11,1,"j","j",4.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,13,19,1,"j","j",6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,4,13,20,1,"j","j",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,5,14,5,1,"j","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,5,14,13,1,"j","j",7.3,null,null,17,null,null,{"$f":"IF(($L8362-$I8362)/(($C$4-$C$16))>=O$21,1*$F8362,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,12,5,14,19,1,"j","j",6.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,15,6,1,"j","n",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,15,16,1,"j","n",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,15,23,1,"j","n",6.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,7,16,6,1,"j","n",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,7,16,8,1,"j","n",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,7,16,17,1,"j","n",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,1,17,5,1,"j","j",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,17,10,1,"j","j",1.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,17,19,1,"j","j",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,2,18,3,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,2,18,12,1,"j","j",1.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,2,18,20,1,"j","j",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,3,19,2,{"$f":"IF(AND(B8471>$D$13,B8471<$I$13),0,IF(B8471=$D$13,IF(D8471>=$D$12,0,1),IF(B8471=$I$13,IF(D8471<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C8471=7),AND($I$9=1,C8471>5)),\"n\",IF($I$9=2,G8471,\"j\"))","v":"j"},0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,3,19,5,1,"j","j",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,3,19,16,1,"j","j",5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,19,22,1,"j","j",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,20,6,1,"j","j",-1.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,4,20,15,1,"j","j",3.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,20,23,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,8,1,"j","j",-0.9,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,5,21,9,1,"j","j",-0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,5,21,17,1,"j","j",1.9,null,null,{"$f":"IF(AND(H8534=\"j\",OR(AND($C$9<=E8534,E8534<$C$10),AND($D$9<=E8534,E8534<$D$10))),$J$5,$C$5)*F8534","v":17},null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,18,{"$f":"IF(AND(B8535>$D$13,B8535<$I$13),0,IF(B8535=$D$13,IF(D8535>=$D$12,0,1),IF(B8535=$I$13,IF(D8535<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C8535=7),AND($I$9=1,C8535>5)),\"n\",IF($I$9=2,G8535,\"j\"))","v":"j"},1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,19,1,"j","j",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,20,1,"j","j",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,21,1,"j","j",1.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,22,1,"j","j",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,23,1,"j","j",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,24,1,"j","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,1,1,"j","n",3,null,null,16,null,null,{"$f":"IF(($L8542-$I8542)/(($C$4-$C$16))>=O$21,1*$F8542,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,2,1,"j","n",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,3,1,"j","n",4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,4,1,"j","n",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,5,1,"j","n",4.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,6,1,"j","n",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,7,1,"j","n",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,8,1,"j","n",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,22,9,1,"j","n",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,22,10,1,"j","n",6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,22,11,1,"j","n",6.2,null,null,16,null,null,{"$f":"IF(($L8552-$I8552)/(($C$4-$C$16))>=O$21,1*$F8552,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,12,6,22,12,1,"j","n",6.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,22,13,1,"j","n",6.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,22,14,1,"j","n",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,22,15,1,"j","n",7.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,22,16,1,"j","n",7.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,22,17,1,"j","n",7.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,22,18,1,"j","n",8.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,6,22,19,1,"j","n",8.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,6,22,20,1,"j","n",9.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,6,22,21,1,"j","n",9.6,null,null,16,null,null,{"$f":"IF(($L8562-$I8562)/(($C$4-$C$16))>=O$21,1*$F8562,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,12,6,22,22,1,"j","n",10,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,6,22,23,1,"j","n",10.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,6,22,24,1,"j","n",10.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,1,1,"j","n",11.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,2,1,"j","n",11.5,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,3,1,"j","n",11.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,4,1,"j","n",12,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,5,1,"j","n",12.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,6,1,"j","n",12.5,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,7,1,"j","n",12.5,null,null,16,null,null,{"$f":"IF(($L8572-$I8572)/(($C$4-$C$16))>=O$21,1*$F8572,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,8,1,"j","n",12.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,9,1,"j","n",12.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,10,1,"j","n",13,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,11,1,"j","n",13.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,12,1,"j","n",13.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,13,1,"j","n",13.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,14,1,"j","n",12.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,15,1,"j","n",12.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,16,1,"j","n",12.5,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,17,1,"j","n",12.5,null,null,16,null,null,{"$f":"IF(($L8582-$I8582)/(($C$4-$C$16))>=O$21,1*$F8582,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,18,1,"j","n",12.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,19,1,"j","n",12.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,20,1,"j","n",12,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,21,1,"j","n",11.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,22,1,"j","n",11.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,23,1,"j","n",11.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,7,23,24,1,"j","n",11.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,1,24,1,1,"j","j",10.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,12,1,24,2,1,"j","j",10.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,1,24,3,1,"j","j",10.1,null,null,16,null,null,{"$f":"IF(($L8592-$I8592)/(($C$4-$C$16))>=O$21,1*$F8592,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,12,1,24,4,1,"j","j",9.6999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,1,24,5,1,"j","j",9.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,1,24,6,1,"j","j",9.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,1,24,7,1,"j","j",9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,1,24,8,1,"j","j",8.9,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,1,24,9,1,"j","j",8.6999999999999993,null,null,{"$f":"IF(AND(H8598=\"j\",OR(AND($C$9<=E8598,E8598<$C$10),AND($D$9<=E8598,E8598<$D$10))),$J$5,$C$5)*F8598","v":17},null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,1,24,10,{"$f":"IF(AND(B8599>$D$13,B8599<$I$13),0,IF(B8599=$D$13,IF(D8599>=$D$12,0,1),IF(B8599=$I$13,IF(D8599<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C8599=7),AND($I$9=1,C8599>5)),\"n\",IF($I$9=2,G8599,\"j\"))","v":"j"},8.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,1,24,11,1,"j","j",8.3000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,1,24,12,1,"j","j",8.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,1,24,13,1,"j","j",8.6999999999999993,null,null,17,null,null,{"$f":"IF(($L8602-$I8602)/(($C$4-$C$16))>=O$21,1*$F8602,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,12,1,24,14,1,"j","j",8.8000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,1,24,15,1,"j","j",8.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,1,24,16,1,"j","j",8.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,1,24,17,1,"j","j",8.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,1,24,18,1,"j","j",8.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,1,24,19,1,"j","j",8.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,1,24,20,1,"j","j",8.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,1,24,21,1,"j","j",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,12,1,24,22,1,"j","j",7.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,1,24,23,1,"j","j",7.6,null,null,16,null,null,{"$f":"IF(($L8612-$I8612)/(($C$4-$C$16))>=O$21,1*$F8612,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,12,1,24,24,1,"j","j",7.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,1,1,"n","j",7.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,2,1,"n","j",7.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,3,1,"n","j",7.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,4,1,"n","j",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,5,1,"n","j",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,6,1,"n","j",6.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,7,1,"n","j",6.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,8,1,"n","j",6.7,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,9,1,"n","j",6.7,null,null,17,null,null,{"$f":"IF(($L8622-$I8622)/(($C$4-$C$16))>=O$21,1*$F8622,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,10,1,"n","j",6.7,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,11,1,"n","j",6.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,12,1,"n","j",6.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,13,1,"n","j",6.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,14,1,"n","j",6.3,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,15,1,"n","j",6.1,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,2,25,16,1,"n","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,2,25,17,1,"n","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,2,25,18,1,"n","j",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,19,1,"n","j",5.6,null,null,16,null,null,{"$f":"IF(($L8632-$I8632)/(($C$4-$C$16))>=O$21,1*$F8632,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,20,1,"n","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,21,1,"n","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,22,1,"n","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,23,1,"n","j",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,2,25,24,1,"n","j",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,3,26,1,1,"n","j",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,3,26,2,1,"n","j",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,3,26,3,1,"n","j",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,4,1,"n","j",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,5,1,"n","j",5,null,null,16,null,null,{"$f":"IF(($L8642-$I8642)/(($C$4-$C$16))>=O$21,1*$F8642,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,6,1,"n","j",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,3,26,7,1,"n","j",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,3,26,8,1,"n","j",6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,9,1,"n","j",6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,10,1,"n","j",5.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,11,1,"n","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,12,1,"n","j",6.1,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,13,1,"n","j",6.1,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,14,1,"n","j",6.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,15,1,"n","j",6.5,null,null,17,null,null,{"$f":"IF(($L8652-$I8652)/(($C$4-$C$16))>=O$21,1*$F8652,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,12,3,26,16,1,"n","j",6.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,17,1,"n","j",5.7,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,18,1,"n","j",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,3,26,19,1,"n","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,3,26,20,1,"n","j",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,3,26,21,1,"n","j",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,22,1,"n","j",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,23,1,"n","j",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,26,24,1,"n","j",4.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,1,1,"n","j",3.9,null,null,{"$f":"IF(AND(H8662=\"j\",OR(AND($C$9<=E8662,E8662<$C$10),AND($D$9<=E8662,E8662<$D$10))),$J$5,$C$5)*F8662","v":16},null,null,{"$f":"IF(($L8662-$I8662)/(($C$4-$C$16))>=O$21,1*$F8662,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,2,{"$f":"IF(AND(B8663>$D$13,B8663<$I$13),0,IF(B8663=$D$13,IF(D8663>=$D$12,0,1),IF(B8663=$I$13,IF(D8663<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C8663=7),AND($I$9=1,C8663>5)),\"n\",IF($I$9=2,G8663,\"j\"))","v":"j"},3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,3,1,"n","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,4,1,"n","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,5,1,"n","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,6,1,"n","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,7,1,"n","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,8,1,"n","j",4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,9,1,"n","j",4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,10,1,"n","j",3.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,11,1,"n","j",3.5,null,null,17,null,null,{"$f":"IF(($L8672-$I8672)/(($C$4-$C$16))>=O$21,1*$F8672,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,12,1,"n","j",5.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,13,1,"n","j",5.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,14,1,"n","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,15,1,"n","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,16,1,"n","j",5.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,17,1,"n","j",5.4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,18,1,"n","j",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,19,1,"n","j",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,20,1,"n","j",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,21,1,"n","j",5.2,null,null,16,null,null,{"$f":"IF(($L8682-$I8682)/(($C$4-$C$16))>=O$21,1*$F8682,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,22,1,"n","j",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,23,1,"n","j",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,27,24,1,"n","j",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,5,28,1,1,"n","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,5,28,2,1,"n","j",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,5,28,3,1,"n","j",6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,5,28,4,1,"n","j",6.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,5,28,5,1,"n","j",6.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,5,28,6,1,"n","j",7.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,5,28,7,1,"n","j",7.4,null,null,16,null,null,{"$f":"IF(($L8692-$I8692)/(($C$4-$C$16))>=O$21,1*$F8692,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,12,5,28,8,1,"n","j",7.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,5,28,9,1,"n","j",7.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,5,28,10,1,"n","j",6.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,5,28,11,1,"n","j",5.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,28,12,1,"n","j",5.5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,28,13,1,"n","j",5.7,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,28,14,1,"n","j",6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,28,15,1,"n","j",6.1,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,28,16,1,"n","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,28,17,1,"n","j",5.2,null,null,17,null,null,{"$f":"IF(($L8702-$I8702)/(($C$4-$C$16))>=O$21,1*$F8702,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,12,5,28,18,1,"n","j",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,28,19,1,"n","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,28,20,1,"n","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,28,21,1,"n","j",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,28,22,1,"n","j",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,28,23,1,"n","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,28,24,1,"n","j",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,29,1,1,"n","n",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,2,1,"n","n",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,3,1,"n","n",2.1,null,null,16,null,null,{"$f":"IF(($L8712-$I8712)/(($C$4-$C$16))>=O$21,1*$F8712,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,4,1,"n","n",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,5,1,"n","n",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,6,1,"n","n",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,7,1,"n","n",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,8,1,"n","n",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,9,1,"n","n",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,10,1,"n","n",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,11,1,"n","n",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,12,1,"n","n",2.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,13,1,"n","n",2.5,null,null,16,null,null,{"$f":"IF(($L8722-$I8722)/(($C$4-$C$16))>=O$21,1*$F8722,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,14,1,"n","n",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,29,15,1,"n","n",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,29,16,1,"n","n",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,29,17,1,"n","n",4.0999999999999996,null,null,{"$f":"IF(AND(H8726=\"j\",OR(AND($C$9<=E8726,E8726<$C$10),AND($D$9<=E8726,E8726<$D$10))),$J$5,$C$5)*F8726","v":16},null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,29,18,{"$f":"IF(AND(B8727>$D$13,B8727<$I$13),0,IF(B8727=$D$13,IF(D8727>=$D$12,0,1),IF(B8727=$I$13,IF(D8727<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C8727=7),AND($I$9=1,C8727>5)),\"n\",IF($I$9=2,G8727,\"j\"))","v":"n"},4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,29,19,1,"n","n",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,29,20,1,"n","n",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,29,21,1,"n","n",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,29,22,1,"n","n",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,29,23,1,"n","n",2.9,null,null,16,null,null,{"$f":"IF(($L8732-$I8732)/(($C$4-$C$16))>=O$21,1*$F8732,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,12,6,29,24,1,"n","n",2.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,1,1,"n","n",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,2,1,"n","n",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,3,1,"n","n",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,4,1,"n","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,5,1,"n","n",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,6,1,"n","n",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,7,1,"n","n",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,8,1,"n","n",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,9,1,"n","n",1.4,null,null,16,null,null,{"$f":"IF(($L8742-$I8742)/(($C$4-$C$16))>=O$21,1*$F8742,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,10,1,"n","n",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,11,1,"n","n",1.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,12,1,"n","n",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,13,1,"n","n",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,30,14,1,"n","n",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,30,15,1,"n","n",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,30,16,1,"n","n",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,30,17,1,"n","n",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,30,18,1,"n","n",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,30,19,1,"n","n",3.2,null,null,16,null,null,{"$f":"IF(($L8752-$I8752)/(($C$4-$C$16))>=O$21,1*$F8752,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,12,7,30,20,1,"n","n",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,30,21,1,"n","n",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,30,22,1,"n","n",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,30,23,1,"n","n",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,30,24,1,"n","n",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,31,1,1,"n","j",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,31,2,1,"n","j",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,31,3,1,"n","j",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,31,4,1,"n","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,31,5,1,"n","j",4.0999999999999996,null,null,16,null,null,{"$f":"IF(($L8762-$I8762)/(($C$4-$C$16))>=O$21,1*$F8762,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,12,1,31,6,1,"n","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,31,7,1,"n","j",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,31,8,1,"n","j",2.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,9,1,"n","j",2.1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,10,1,"n","j",2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,11,1,"n","j",2.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,12,1,"n","j",3.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,13,1,"n","j",3.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,31,14,1,"n","j",3.3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,15,1,"n","j",2.2000000000000002,null,null,17,null,null,{"$f":"IF(($L8772-$I8772)/(($C$4-$C$16))>=O$21,1*$F8772,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,16,1,"n","j",1.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,17,1,"n","j",1.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,18,1,"n","j",1.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,19,1,"n","j",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,20,1,"n","j",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,21,1,"n","j",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,22,1,"n","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,23,1,"n","j",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,31,24,1,"n","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(O22:O8781)","v":0},6,50,176,488,1201,2263,3600,4539,5259,5600]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Ces données sont rapatriées dans le cadre 4 de l'onglet \"Rendement saisonnier\""]

{"sheet":"Fichier météo StHubert","index":4,"n_rows":8783,"n_cols":25,"rows_kept":2250,"cut":true,"hidden":true,"merged":[[17,1,18,1],[17,11,18,11],[17,8,18,8],[17,4,18,4],[17,3,18,3],[17,2,18,2]],"bounds":{"rows_first":1000,"rows_last":250,"rows_between":1000,"halvings":1}}
[]
[null,"Etablissement de la monotone de chaleur"]
[]
[null,"T° cons jour =",{"$f":"'Calcul du rendement'!F42","v":19},"°C","Gain de température pour apports gratuits :",null,null,null,null,{"$f":"'Calcul du rendement'!F44","v":2},"°C","Température extérieure moyenne sur l'année",null,null,null,null,null,{"$f":"SUM(I22:I8781)/8760","v":6.7208219178082187},"°C"]
[null,"T° cons nuit =",{"$f":"'Calcul du rendement'!F43","v":16},"°C","Température de jour effective :",null,null,null,null,{"$f":"C4-J4","v":17},"°C","Température extérieure moyenne saison de chauffe",null,null,null,null,null,{"$f":"(SUM(I22:I3237)+SUM(I6190:I8781))/5800","v":3.5846896551724106},"°C","soit du 15 septembre au 15 mai"]
[null,null,null,null,null,null,null,null,null,null,null,"Température extérieure moyenne hors saison de chauffe",null,null,null,null,null,{"$f":"SUM(I3238:I6190)/2960","v":12.869189189189193},"°C","soit du 15 mai au 15 septembre"]
[null,null,"Plage 1","Plage 2"]
[null,null,true,false]
[null,"Heure début",{"$f":"IF($C$8,'Calcul du rendement'!F36,0)","v":8},{"$f":"IF($D$8,'Calcul du rendement'!$F$37,0)","v":0},"h",null,"Horaire hebdomadaire :",null,1]
[null,"Heure fin",{"$f":"IF($C$8,'Calcul du rendement'!H36,0)","v":18},{"$f":"IF($D$8,'Calcul du rendement'!H37,0)","v":0},"h"]
[]
[null,"Jour arrêt chauffage",null,{"$f":"'Calcul du rendement'!E50","v":15},null,null,"Jour début chauffage",null,{"$f":"'Calcul du rendement'!E51","v":15}]
[null,"Mois arrêt chauffage",null,{"$f":"'Calcul du rendement'!F50","v":5},null,null,"Mois début chauffage",null,{"$f":"'Calcul du rendement'!F51","v":9}]
[]
[]
[null,"T° de base",{"$f":"'Calcul du rendement'!G20","v":-8},"°C"]
[]
[null,"Mois","Semaine","Jour","Heure","Saison","Horaire","Horaire","T° ext. ",null,null,"T° int."]
[null,null,null,null,null,"chauffe","école","hebdomadaire",null,null,null,null,null,null,null,null,null,null,null,"Monotone de chaleur"]
[null,null,null,null,null,{"$f":"SUM(F22:F8781)","v":5808},null,null,null,null,null,null,null,"Formule :","= 1 x Saison de chauffe si (Tint - Text) / (Tconsigne - Tbase) > %Puissance"]
[null,null,null,null,null,"[h]",null,null,"[°C]",null,null,"[°C]",null,"% Puissance",1,{"$f":"0.9","v":0.9},0.8,0.7,0.6,0.5,0.4,0.3,0.2,0.1,0]
[null,1,1,1,1,{"$f":"IF(AND(B22>$D$13,B22<$I$13),0,IF(B22=$D$13,IF(D22>=$D$12,0,1),IF(B22=$I$13,IF(D22<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C22=7),AND($I$9=1,C22>5)),\"n\",IF($I$9=2,G22,\"j\"))","v":"j"},-2.4,null,null,{"$f":"IF(AND(H22=\"j\",OR(AND($C$9<=E22,E22<$C$10),AND($D$9<=E22,E22<$D$10))),$J$5,$C$5)*F22","v":16},null,null,{"$f":"IF(($L22-$I22)/(($C$4-$C$16))>=O$21,1*$F22,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,1,1,2,{"$f":"IF(AND(B23>$D$13,B23<$I$13),0,IF(B23=$D$13,IF(D23>=$D$12,0,1),IF(B23=$I$13,IF(D23<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C23=7),AND($I$9=1,C23>5)),\"n\",IF($I$9=2,G23,\"j\"))","v":"j"},-2.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,1,3,1,"n","j",-2.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,1,4,1,"n","j",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,5,1,"n","j",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,6,1,"n","j",-3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,7,1,"n","j",-3.1,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,8,1,"n","j",-3.1,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,9,1,"n","j",-3.4,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,10,1,"n","j",-3.7,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,11,1,"n","j",-3.7,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,12,1,"n","j",-3.4,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,13,1,"n","j",-3,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,14,1,"n","j",-2.8,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,15,1,"n","j",-2.9,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,16,1,"n","j",-2.9,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,17,1,"n","j",-3,null,null,17,null,null,{"$f":"IF(($L38-$I38)/(($C$4-$C$16))>=O$21,1*$F38,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,18,1,"n","j",-3.1,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,19,1,"n","j",-3.4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,20,1,"n","j",-3.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,21,1,"n","j",-3.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,22,1,"n","j",-3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,23,1,"n","j",-3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,1,1,24,1,"n","j",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,2,1,1,"n","j",-2.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,2,2,1,"n","j",-2.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,2,3,1,"n","j",-2.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,2,4,1,"n","j",-2.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,2,5,1,"n","j",-2.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,2,6,1,"n","j",-2.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,2,7,1,"n","j",-2.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,2,8,1,"n","j",-2.4,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,2,9,1,"n","j",-2.4,null,null,17,null,null,{"$f":"IF(($L54-$I54)/(($C$4-$C$16))>=O$21,1*$F54,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,2,2,10,1,"n","j",-2.5,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,2,11,1,"n","j",-2.5,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,2,12,1,"n","j",-2.2999999999999998,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,2,13,1,"n","j",-2.2000000000000002,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,2,14,1,"n","j",-2.2000000000000002,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,2,15,1,"n","j",-2.2000000000000002,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,2,16,1,"n","j",-2.2000000000000002,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,2,17,1,"n","j",-2.1,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,2,18,1,"n","j",-2.1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,2,19,1,"n","j",-2.1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,2,20,1,"n","j",-2.2000000000000002,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,2,21,1,"n","j",-2.2999999999999998,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,2,22,1,"n","j",-2.2999999999999998,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,2,23,1,"n","j",-2.2999999999999998,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,2,24,1,"n","j",-2.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,3,1,1,"n","j",-2.8,null,null,16,null,null,{"$f":"IF(($L70-$I70)/(($C$4-$C$16))>=O$21,1*$F70,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,3,3,2,1,"n","j",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,3,1,"n","j",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,4,1,"n","j",-2.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,3,5,1,"n","j",-2.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,3,6,1,"n","j",-2.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,3,7,1,"n","j",-2.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,3,8,1,"n","j",-2.7,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,9,1,"n","j",-2.6,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,10,1,"n","j",-2.5,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,11,1,"n","j",-2.2999999999999998,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,12,1,"n","j",-2,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,13,1,"n","j",-1.9,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,14,1,"n","j",-1.9,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,15,1,"n","j",-2.1,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,16,1,"n","j",-2.4,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,17,1,"n","j",-2.9,null,null,{"$f":"IF(AND(H86=\"j\",OR(AND($C$9<=E86,E86<$C$10),AND($D$9<=E86,E86<$D$10))),$J$5,$C$5)*F86","v":17},null,null,{"$f":"IF(($L86-$I86)/(($C$4-$C$16))>=O$21,1*$F86,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,18,{"$f":"IF(AND(B87>$D$13,B87<$I$13),0,IF(B87=$D$13,IF(D87>=$D$12,0,1),IF(B87=$I$13,IF(D87<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C87=7),AND($I$9=1,C87>5)),\"n\",IF($I$9=2,G87,\"j\"))","v":"j"},-3.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,19,1,"n","j",-3.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,20,1,"n","j",-3.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,21,1,"n","j",-3.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,22,1,"n","j",-3.7,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,23,1,"n","j",-3.7,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,3,24,1,"n","j",-3.7,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,4,1,1,"n","j",-3.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,4,2,1,"n","j",-3.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,4,3,1,"n","j",-3.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,4,4,1,"n","j",-3.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,4,5,1,"n","j",-3.8,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,4,6,1,"n","j",-3.2,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,4,7,1,"n","j",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,4,8,1,"n","j",-3.1,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,4,9,1,"n","j",-2.9,null,null,17,null,null,{"$f":"IF(($L102-$I102)/(($C$4-$C$16))>=O$21,1*$F102,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,4,4,10,1,"n","j",-2.7,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,4,11,1,"n","j",-2.2999999999999998,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,4,12,1,"n","j",-1.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,4,13,1,"n","j",-1.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,4,14,1,"n","j",-1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,4,15,1,"n","j",-0.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,4,16,1,"n","j",-0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,4,17,1,"n","j",0,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,4,18,1,"n","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,19,1,"n","j",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,20,1,"n","j",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,21,1,"n","j",0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,22,1,"n","j",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,23,1,"n","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,4,24,1,"n","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,1,1,"n","j",0.7,null,null,16,null,null,{"$f":"IF(($L118-$I118)/(($C$4-$C$16))>=O$21,1*$F118,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,2,1,"n","j",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,3,1,"n","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,4,1,"n","j",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,5,1,"n","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,6,1,"n","j",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,7,1,"n","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,8,1,"n","j",0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,9,1,"n","j",0.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,10,1,"n","j",0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,11,1,"n","j",0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,12,1,"n","j",0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,13,1,"n","j",0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,14,1,"n","j",0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,15,1,"n","j",0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,16,1,"n","j",0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,17,1,"n","j",0.7,null,null,17,null,null,{"$f":"IF(($L134-$I134)/(($C$4-$C$16))>=O$21,1*$F134,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,5,5,18,1,"n","j",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,19,1,"n","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,20,1,"n","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,21,1,"n","j",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,22,1,"n","j",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,23,1,"n","j",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,5,24,1,"n","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,1,1,"n","n",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,2,1,"n","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,3,1,"n","n",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,4,1,"n","n",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,5,1,"n","n",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,6,1,"n","n",0.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,7,1,"n","n",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,8,1,"n","n",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,9,1,"n","n",0.6,null,null,{"$f":"IF(AND(H150=\"j\",OR(AND($C$9<=E150,E150<$C$10),AND($D$9<=E150,E150<$D$10))),$J$5,$C$5)*F150","v":16},null,null,{"$f":"IF(($L150-$I150)/(($C$4-$C$16))>=O$21,1*$F150,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,10,{"$f":"IF(AND(B151>$D$13,B151<$I$13),0,IF(B151=$D$13,IF(D151>=$D$12,0,1),IF(B151=$I$13,IF(D151<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C151=7),AND($I$9=1,C151>5)),\"n\",IF($I$9=2,G151,\"j\"))","v":"n"},0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,11,1,"n","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,12,1,"n","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,13,1,"n","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,14,1,"n","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,15,1,"n","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,16,1,"n","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,17,1,"n","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,18,1,"n","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,19,1,"n","n",0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,20,1,"n","n",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,21,1,"n","n",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,22,1,"n","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,23,1,"n","n",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,6,24,1,"n","n",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,1,1,"n","n",0.6,null,null,16,null,null,{"$f":"IF(($L166-$I166)/(($C$4-$C$16))>=O$21,1*$F166,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,2,1,"n","n",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,3,1,"n","n",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,4,1,"n","n",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,5,1,"n","n",0.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,6,1,"n","n",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,7,1,"n","n",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,8,1,"n","n",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,9,1,"n","n",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,10,1,"n","n",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,11,1,"n","n",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,12,1,"n","n",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,13,1,"n","n",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,14,1,"n","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,15,1,"n","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,16,1,"n","n",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,17,1,"n","n",1.2,null,null,16,null,null,{"$f":"IF(($L182-$I182)/(($C$4-$C$16))>=O$21,1*$F182,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,18,1,"n","n",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,19,1,"n","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,20,1,"n","n",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,21,1,"n","n",0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,22,1,"n","n",0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,23,1,"n","n",0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,7,24,1,"n","n",0.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,1,1,"j","j",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,2,1,"j","j",0.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,3,1,"j","j",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,4,1,"j","j",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,5,1,"j","j",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,6,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,7,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,8,1,"j","j",0,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,8,9,1,"j","j",-0.1,null,null,17,null,null,{"$f":"IF(($L198-$I198)/(($C$4-$C$16))>=O$21,1*$F198,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,1,8,10,1,"j","j",-0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,8,11,1,"j","j",0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,8,12,1,"j","j",0.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,8,13,1,"j","j",0.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,8,14,1,"j","j",0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,8,15,1,"j","j",0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,8,16,1,"j","j",0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,8,17,1,"j","j",0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,8,18,1,"j","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,19,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,20,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,21,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,22,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,23,1,"j","j",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,8,24,1,"j","j",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,1,1,"j","j",-0.2,null,null,{"$f":"IF(AND(H214=\"j\",OR(AND($C$9<=E214,E214<$C$10),AND($D$9<=E214,E214<$D$10))),$J$5,$C$5)*F214","v":16},null,null,{"$f":"IF(($L214-$I214)/(($C$4-$C$16))>=O$21,1*$F214,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,2,{"$f":"IF(AND(B215>$D$13,B215<$I$13),0,IF(B215=$D$13,IF(D215>=$D$12,0,1),IF(B215=$I$13,IF(D215<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C215=7),AND($I$9=1,C215>5)),\"n\",IF($I$9=2,G215,\"j\"))","v":"j"},-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,3,1,"j","j",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,4,1,"j","j",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,5,1,"j","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,6,1,"j","j",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,7,1,"j","j",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,8,1,"j","j",-1.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,9,1,"j","j",-1.6,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,10,1,"j","j",-1.6,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,11,1,"j","j",-1.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,12,1,"j","j",-1.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,13,1,"j","j",-1.6,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,14,1,"j","j",-1.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,15,1,"j","j",-1.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,9,16,1,"j","j",-2.2999999999999998,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,17,1,"j","j",-2.8,null,null,17,null,null,{"$f":"IF(($L230-$I230)/(($C$4-$C$16))>=O$21,1*$F230,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,18,1,"j","j",-3.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,19,1,"j","j",-3.6,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,20,1,"j","j",-3.7,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,21,1,"j","j",-3.8,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,22,1,"j","j",-3.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,23,1,"j","j",-4.2,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,9,24,1,"j","j",-4.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,1,1,"j","j",-4.5999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,2,1,"j","j",-4.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,3,1,"j","j",-3.7,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,4,1,"j","j",-3.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,5,1,"j","j",-3.2,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,6,1,"j","j",-3.4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,7,1,"j","j",-3.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,8,1,"j","j",-4.7,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,10,9,1,"j","j",-5.2,null,null,17,null,null,{"$f":"IF(($L246-$I246)/(($C$4-$C$16))>=O$21,1*$F246,0)","v":0},0,1,1,1,1,1,1,1,1,1]
[null,1,3,10,10,1,"j","j",-4.9000000000000004,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,10,11,1,"j","j",-4.3,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,12,1,"j","j",-3.9,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,13,1,"j","j",-3.7,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,14,1,"j","j",-3.4,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,15,1,"j","j",-3.3,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,16,1,"j","j",-3.5,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,17,1,"j","j",-3.8,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,18,1,"j","j",-4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,19,1,"j","j",-4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,20,1,"j","j",-4.0999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,21,1,"j","j",-4.2,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,22,1,"j","j",-4.4000000000000004,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,23,1,"j","j",-4.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,10,24,1,"j","j",-4.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,11,1,1,"j","j",-4.5,null,null,16,null,null,{"$f":"IF(($L262-$I262)/(($C$4-$C$16))>=O$21,1*$F262,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,4,11,2,1,"j","j",-4.5999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,11,3,1,"j","j",-4.8,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,11,4,1,"j","j",-4.9000000000000004,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,11,5,1,"j","j",-5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,11,6,1,"j","j",-5.0999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,11,7,1,"j","j",-5.2,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,11,8,1,"j","j",-5.0999999999999996,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,9,1,"j","j",-5.0999999999999996,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,10,1,"j","j",-5.2,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,11,1,"j","j",-5.3,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,12,1,"j","j",-5.3,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,13,1,"j","j",-5.2,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,14,1,"j","j",-5,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,15,1,"j","j",-4.8,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,16,1,"j","j",-4.8,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,17,1,"j","j",-4.9000000000000004,null,null,{"$f":"IF(AND(H278=\"j\",OR(AND($C$9<=E278,E278<$C$10),AND($D$9<=E278,E278<$D$10))),$J$5,$C$5)*F278","v":17},null,null,{"$f":"IF(($L278-$I278)/(($C$4-$C$16))>=O$21,1*$F278,0)","v":0},0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,18,{"$f":"IF(AND(B279>$D$13,B279<$I$13),0,IF(B279=$D$13,IF(D279>=$D$12,0,1),IF(B279=$I$13,IF(D279<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C279=7),AND($I$9=1,C279>5)),\"n\",IF($I$9=2,G279,\"j\"))","v":"j"},-5.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,11,19,1,"j","j",-5.6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,20,1,"j","j",-5.7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,21,1,"j","j",-5.8,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,22,1,"j","j",-5.8,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,23,1,"j","j",-5.9,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,11,24,1,"j","j",-6.2,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,1,1,"j","j",-6.7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,2,1,"j","j",-6.8,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,3,1,"j","j",-6.9,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,4,1,"j","j",-7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,5,1,"j","j",-7.4,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,6,1,"j","j",-8.4,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,5,12,7,1,"j","j",-9.1,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,5,12,8,1,"j","j",-9.4,null,null,17,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,5,12,9,1,"j","j",-9.6,null,null,17,null,null,{"$f":"IF(($L294-$I294)/(($C$4-$C$16))>=O$21,1*$F294,0)","v":0},1,1,1,1,1,1,1,1,1,1]
[null,1,5,12,10,1,"j","j",-9.1999999999999993,null,null,17,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,5,12,11,1,"j","j",-8.1999999999999993,null,null,17,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,5,12,12,1,"j","j",-7.2,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,13,1,"j","j",-6.3,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,14,1,"j","j",-5.9,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,15,1,"j","j",-5.6,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,16,1,"j","j",-5.6,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,17,1,"j","j",-6.1,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,18,1,"j","j",-6.7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,19,1,"j","j",-7.5,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,20,1,"j","j",-8.1999999999999993,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,5,12,21,1,"j","j",-8.6,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,5,12,22,1,"j","j",-8.8000000000000007,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,5,12,23,1,"j","j",-9.1,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,5,12,24,1,"j","j",-9.3000000000000007,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,6,13,1,1,"j","n",-9.6,null,null,16,null,null,{"$f":"IF(($L310-$I310)/(($C$4-$C$16))>=O$21,1*$F310,0)","v":0},1,1,1,1,1,1,1,1,1,1]
[null,1,6,13,2,1,"j","n",-9.4,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,6,13,3,1,"j","n",-9.1999999999999993,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,6,13,4,1,"j","n",-8.1999999999999993,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,6,13,5,1,"j","n",-8.4,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,6,13,6,1,"j","n",-9.6,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,6,13,7,1,"j","n",-9.6999999999999993,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,6,13,8,1,"j","n",-9.8000000000000007,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,6,13,9,1,"j","n",-9.1,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,6,13,10,1,"j","n",-8.6999999999999993,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,6,13,11,1,"j","n",-7.4,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,6,13,12,1,"j","n",-5.4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,13,13,1,"j","n",-4.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,13,14,1,"j","n",-3.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,13,15,1,"j","n",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,13,16,1,"j","n",-2.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,13,17,1,"j","n",-3,null,null,16,null,null,{"$f":"IF(($L326-$I326)/(($C$4-$C$16))>=O$21,1*$F326,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,6,13,18,1,"j","n",-3.7,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,13,19,1,"j","n",-4.8,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,13,20,1,"j","n",-5.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,13,21,1,"j","n",-5.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,13,22,1,"j","n",-6.3,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,6,13,23,1,"j","n",-7.3,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,6,13,24,1,"j","n",-7.7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,14,1,1,"j","n",-8.6,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,2,1,"j","n",-8.9,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,3,1,"j","n",-9.6999999999999993,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,4,1,"j","n",-9.8000000000000007,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,5,1,"j","n",-9.6,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,6,1,"j","n",-9.6999999999999993,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,7,1,"j","n",-9.3000000000000007,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,8,1,"j","n",-8.8000000000000007,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,9,1,"j","n",-8.6,null,null,{"$f":"IF(AND(H342=\"j\",OR(AND($C$9<=E342,E342<$C$10),AND($D$9<=E342,E342<$D$10))),$J$5,$C$5)*F342","v":16},null,null,{"$f":"IF(($L342-$I342)/(($C$4-$C$16))>=O$21,1*$F342,0)","v":0},1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,10,{"$f":"IF(AND(B343>$D$13,B343<$I$13),0,IF(B343=$D$13,IF(D343>=$D$12,0,1),IF(B343=$I$13,IF(D343<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C343=7),AND($I$9=1,C343>5)),\"n\",IF($I$9=2,G343,\"j\"))","v":"n"},-8.3000000000000007,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,11,1,"j","n",-7.6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,14,12,1,"j","n",-7.1,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,14,13,1,"j","n",-6.7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,14,14,1,"j","n",-6.2,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,14,15,1,"j","n",-6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,14,16,1,"j","n",-6.3,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,14,17,1,"j","n",-6.9,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,14,18,1,"j","n",-7.8,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,7,14,19,1,"j","n",-8.4,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,20,1,"j","n",-8.6,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,21,1,"j","n",-8.6999999999999993,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,22,1,"j","n",-8.5,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,23,1,"j","n",-8.5,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,7,14,24,1,"j","n",-8.6999999999999993,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,1,1,"j","j",-8.6,null,null,16,null,null,{"$f":"IF(($L358-$I358)/(($C$4-$C$16))>=O$21,1*$F358,0)","v":0},1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,2,1,"j","j",-9,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,3,1,"j","j",-9.4,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,4,1,"j","j",-9.1999999999999993,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,5,1,"j","j",-9.6,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,6,1,"j","j",-10.4,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,7,1,"j","j",-11,null,null,16,null,null,1,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,8,1,"j","j",-11.5,null,null,17,null,null,1,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,9,1,"j","j",-11.9,null,null,17,null,null,1,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,10,1,"j","j",-11.3,null,null,17,null,null,1,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,11,1,"j","j",-8.8000000000000007,null,null,17,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,12,1,"j","j",-6.5,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,1,15,13,1,"j","j",-5.6,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,1,15,14,1,"j","j",-5.8,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,1,15,15,1,"j","j",-6.6,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,1,15,16,1,"j","j",-7.6,null,null,17,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,17,1,"j","j",-8.4,null,null,17,null,null,{"$f":"IF(($L374-$I374)/(($C$4-$C$16))>=O$21,1*$F374,0)","v":0},1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,18,1,"j","j",-8.9,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,19,1,"j","j",-9.3000000000000007,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,20,1,"j","j",-9.4,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,21,1,"j","j",-9.6,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,22,1,"j","j",-9.9,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,23,1,"j","j",-10.1,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,1,15,24,1,"j","j",-10.3,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,16,1,1,"j","j",-9.3000000000000007,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,16,2,1,"j","j",-9,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,16,3,1,"j","j",-8.6,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,16,4,1,"j","j",-8.6,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,16,5,1,"j","j",-8.8000000000000007,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,16,6,1,"j","j",-8.8000000000000007,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,16,7,1,"j","j",-9.1,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,16,8,1,"j","j",-9.4,null,null,17,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,16,9,1,"j","j",-8.8000000000000007,null,null,17,null,null,{"$f":"IF(($L390-$I390)/(($C$4-$C$16))>=O$21,1*$F390,0)","v":0},1,1,1,1,1,1,1,1,1,1]
[null,1,2,16,10,1,"j","j",-7.3,null,null,17,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,2,16,11,1,"j","j",-6,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,2,16,12,1,"j","j",-4.9000000000000004,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,2,16,13,1,"j","j",-3.4,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,16,14,1,"j","j",-2.5,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,16,15,1,"j","j",-2.4,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,16,16,1,"j","j",-2.8,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,16,17,1,"j","j",-3.6,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,16,18,1,"j","j",-4.5999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,16,19,1,"j","j",-5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,16,20,1,"j","j",-4.9000000000000004,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,16,21,1,"j","j",-5.0999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,16,22,1,"j","j",-5.2,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,16,23,1,"j","j",-5.0999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,2,16,24,1,"j","j",-5.2,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,17,1,1,"j","j",-5.3,null,null,{"$f":"IF(AND(H406=\"j\",OR(AND($C$9<=E406,E406<$C$10),AND($D$9<=E406,E406<$D$10))),$J$5,$C$5)*F406","v":16},null,null,{"$f":"IF(($L406-$I406)/(($C$4-$C$16))>=O$21,1*$F406,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,3,17,2,{"$f":"IF(AND(B407>$D$13,B407<$I$13),0,IF(B407=$D$13,IF(D407>=$D$12,0,1),IF(B407=$I$13,IF(D407<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C407=7),AND($I$9=1,C407>5)),\"n\",IF($I$9=2,G407,\"j\"))","v":"j"},-5.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,17,3,1,"j","j",-6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,17,4,1,"j","j",-6.6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,17,5,1,"j","j",-7.1,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,17,6,1,"j","j",-7.5,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,17,7,1,"j","j",-7.9,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,17,8,1,"j","j",-7.8,null,null,17,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,3,17,9,1,"j","j",-7.1,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,17,10,1,"j","j",-6.3,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,17,11,1,"j","j",-5.8,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,17,12,1,"j","j",-4.9000000000000004,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,17,13,1,"j","j",-3.6,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,17,14,1,"j","j",-2.4,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,17,15,1,"j","j",-1.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,17,16,1,"j","j",-1.9,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,17,17,1,"j","j",-2.5,null,null,17,null,null,{"$f":"IF(($L422-$I422)/(($C$4-$C$16))>=O$21,1*$F422,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,3,17,18,1,"j","j",-3.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,17,19,1,"j","j",-4.0999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,17,20,1,"j","j",-5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,3,17,21,1,"j","j",-5.6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,17,22,1,"j","j",-6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,17,23,1,"j","j",-6.3,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,3,17,24,1,"j","j",-6.6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,1,1,"j","j",-7.2,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,2,1,"j","j",-7.3,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,3,1,"j","j",-7.6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,4,1,"j","j",-7.9,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,5,1,"j","j",-8.4,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,4,18,6,1,"j","j",-8.5,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,4,18,7,1,"j","j",-8.6999999999999993,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,4,18,8,1,"j","j",-9,null,null,17,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,4,18,9,1,"j","j",-8.6999999999999993,null,null,17,null,null,{"$f":"IF(($L438-$I438)/(($C$4-$C$16))>=O$21,1*$F438,0)","v":0},1,1,1,1,1,1,1,1,1,1]
[null,1,4,18,10,1,"j","j",-8.1,null,null,17,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,4,18,11,1,"j","j",-7.4,null,null,17,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,1,4,18,12,1,"j","j",-6.7,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,13,1,"j","j",-6,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,14,1,"j","j",-5.6,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,15,1,"j","j",-5.4,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,16,1,"j","j",-5.2,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,17,1,"j","j",-5.0999999999999996,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,18,1,"j","j",-5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,18,19,1,"j","j",-5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,18,20,1,"j","j",-5.7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,21,1,"j","j",-6.1,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,22,1,"j","j",-5.7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,1,4,18,23,1,"j","j",-5.0999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,4,18,24,1,"j","j",-4.8,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,5,19,1,1,"j","j",-4.0999999999999996,null,null,16,null,null,{"$f":"IF(($L454-$I454)/(($C$4-$C$16))>=O$21,1*$F454,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,5,19,2,1,"j","j",-4.9000000000000004,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,5,19,3,1,"j","j",-4.9000000000000004,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,5,19,4,1,"j","j",-2.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,19,5,1,"j","j",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,19,6,1,"j","j",-1.1000000000000001,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,19,7,1,"j","j",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,19,8,1,"j","j",-0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,19,9,1,"j","j",-0.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,19,10,1,"j","j",-0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,19,11,1,"j","j",1.6,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,19,12,1,"j","j",2.2000000000000002,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,19,13,1,"j","j",2.6,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,19,14,1,"j","j",2.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,19,15,1,"j","j",3.1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,19,16,1,"j","j",2.6,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,19,17,1,"j","j",1.6,null,null,{"$f":"IF(AND(H470=\"j\",OR(AND($C$9<=E470,E470<$C$10),AND($D$9<=E470,E470<$D$10))),$J$5,$C$5)*F470","v":17},null,null,{"$f":"IF(($L470-$I470)/(($C$4-$C$16))>=O$21,1*$F470,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,5,19,18,{"$f":"IF(AND(B471>$D$13,B471<$I$13),0,IF(B471=$D$13,IF(D471>=$D$12,0,1),IF(B471=$I$13,IF(D471<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C471=7),AND($I$9=1,C471>5)),\"n\",IF($I$9=2,G471,\"j\"))","v":"j"},0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,19,19,1,"j","j",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,19,20,1,"j","j",-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,19,21,1,"j","j",-1.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,19,22,1,"j","j",-2.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,19,23,1,"j","j",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,5,19,24,1,"j","j",-3.1,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,20,1,1,"j","n",-3.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,20,2,1,"j","n",-3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,20,3,1,"j","n",-2.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,20,4,1,"j","n",-3.4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,20,5,1,"j","n",-4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,20,6,1,"j","n",-3.6,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,20,7,1,"j","n",-3.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,20,8,1,"j","n",-3.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,20,9,1,"j","n",-3.2,null,null,16,null,null,{"$f":"IF(($L486-$I486)/(($C$4-$C$16))>=O$21,1*$F486,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,6,20,10,1,"j","n",-3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,20,11,1,"j","n",-2.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,20,12,1,"j","n",-2.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,20,13,1,"j","n",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,20,14,1,"j","n",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,20,15,1,"j","n",0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,20,16,1,"j","n",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,20,17,1,"j","n",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,6,20,18,1,"j","n",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,20,19,1,"j","n",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,20,20,1,"j","n",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,20,21,1,"j","n",-1.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,20,22,1,"j","n",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,20,23,1,"j","n",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,20,24,1,"j","n",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,1,1,"j","n",-1.5,null,null,16,null,null,{"$f":"IF(($L502-$I502)/(($C$4-$C$16))>=O$21,1*$F502,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,2,1,"j","n",-1.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,3,1,"j","n",-1.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,4,1,"j","n",-1.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,5,1,"j","n",-1.1000000000000001,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,6,1,"j","n",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,7,1,"j","n",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,8,1,"j","n",-0.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,9,1,"j","n",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,10,1,"j","n",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,11,1,"j","n",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,12,1,"j","n",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,13,1,"j","n",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,21,14,1,"j","n",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,15,1,"j","n",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,21,16,1,"j","n",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,21,17,1,"j","n",0,null,null,16,null,null,{"$f":"IF(($L518-$I518)/(($C$4-$C$16))>=O$21,1*$F518,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,7,21,18,1,"j","n",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,21,19,1,"j","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,21,20,1,"j","n",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,21,21,1,"j","n",1.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,21,22,1,"j","n",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,21,23,1,"j","n",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,7,21,24,1,"j","n",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,1,1,"j","j",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,2,1,"j","j",1.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,3,1,"j","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,4,1,"j","j",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,5,1,"j","j",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,6,1,"j","j",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,7,1,"j","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,8,1,"j","j",0.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,9,1,"j","j",0.8,null,null,{"$f":"IF(AND(H534=\"j\",OR(AND($C$9<=E534,E534<$C$10),AND($D$9<=E534,E534<$D$10))),$J$5,$C$5)*F534","v":17},null,null,{"$f":"IF(($L534-$I534)/(($C$4-$C$16))>=O$21,1*$F534,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,1,22,10,{"$f":"IF(AND(B535>$D$13,B535<$I$13),0,IF(B535=$D$13,IF(D535>=$D$12,0,1),IF(B535=$I$13,IF(D535<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C535=7),AND($I$9=1,C535>5)),\"n\",IF($I$9=2,G535,\"j\"))","v":"j"},0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,22,11,1,"j","j",0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,22,12,1,"j","j",0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,22,13,1,"j","j",0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,22,14,1,"j","j",0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,22,15,1,"j","j",1.3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,16,1,"j","j",1.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,17,1,"j","j",1.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,18,1,"j","j",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,19,1,"j","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,20,1,"j","j",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,21,1,"j","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,22,1,"j","j",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,23,1,"j","j",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,22,24,1,"j","j",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,1,1,"j","j",0.8,null,null,16,null,null,{"$f":"IF(($L550-$I550)/(($C$4-$C$16))>=O$21,1*$F550,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,2,1,"j","j",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,3,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,4,1,"j","j",0.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,5,1,"j","j",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,6,1,"j","j",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,7,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,8,1,"j","j",0,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,23,9,1,"j","j",0,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,23,10,1,"j","j",0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,23,11,1,"j","j",0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,23,12,1,"j","j",0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,23,13,1,"j","j",0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,23,14,1,"j","j",0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,2,23,15,1,"j","j",0.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,16,1,"j","j",1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,17,1,"j","j",1,null,null,17,null,null,{"$f":"IF(($L566-$I566)/(($C$4-$C$16))>=O$21,1*$F566,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,18,1,"j","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,19,1,"j","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,20,1,"j","j",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,21,1,"j","j",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,22,1,"j","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,23,1,"j","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,23,24,1,"j","j",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,1,1,"j","j",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,2,1,"j","j",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,3,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,4,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,5,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,6,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,7,1,"j","j",0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,8,1,"j","j",0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,24,9,1,"j","j",0.3,null,null,17,null,null,{"$f":"IF(($L582-$I582)/(($C$4-$C$16))>=O$21,1*$F582,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,3,24,10,1,"j","j",0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,24,11,1,"j","j",0.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,24,12,1,"j","j",0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,24,13,1,"j","j",0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,3,24,14,1,"j","j",0.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,15,1,"j","j",1.1000000000000001,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,16,1,"j","j",1.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,17,1,"j","j",1.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,18,1,"j","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,19,1,"j","j",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,20,1,"j","j",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,21,1,"j","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,22,1,"j","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,23,1,"j","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,3,24,24,1,"j","j",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,25,1,1,"j","j",0,null,null,{"$f":"IF(AND(H598=\"j\",OR(AND($C$9<=E598,E598<$C$10),AND($D$9<=E598,E598<$D$10))),$J$5,$C$5)*F598","v":16},null,null,{"$f":"IF(($L598-$I598)/(($C$4-$C$16))>=O$21,1*$F598,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,4,25,2,{"$f":"IF(AND(B599>$D$13,B599<$I$13),0,IF(B599=$D$13,IF(D599>=$D$12,0,1),IF(B599=$I$13,IF(D599<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C599=7),AND($I$9=1,C599>5)),\"n\",IF($I$9=2,G599,\"j\"))","v":"j"},0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,25,3,1,"j","j",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,25,4,1,"j","j",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,25,5,1,"j","j",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,25,6,1,"j","j",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,25,7,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,25,8,1,"j","j",-0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,25,9,1,"j","j",-0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,25,10,1,"j","j",-0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,25,11,1,"j","j",-0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,25,12,1,"j","j",0,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,25,13,1,"j","j",0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,25,14,1,"j","j",0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,25,15,1,"j","j",0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,25,16,1,"j","j",0,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,25,17,1,"j","j",-0.1,null,null,17,null,null,{"$f":"IF(($L614-$I614)/(($C$4-$C$16))>=O$21,1*$F614,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,4,25,18,1,"j","j",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,4,25,19,1,"j","j",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,25,20,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,25,21,1,"j","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,25,22,1,"j","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,25,23,1,"j","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,4,25,24,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,5,26,1,1,"j","j",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,2,1,"j","j",-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,3,1,"j","j",-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,4,1,"j","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,5,1,"j","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,6,1,"j","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,7,1,"j","j",-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,8,1,"j","j",-0.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,9,1,"j","j",-1,null,null,17,null,null,{"$f":"IF(($L630-$I630)/(($C$4-$C$16))>=O$21,1*$F630,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,10,1,"j","j",-1.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,11,1,"j","j",-1.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,12,1,"j","j",-1.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,13,1,"j","j",-1.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,14,1,"j","j",-1.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,15,1,"j","j",-0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,16,1,"j","j",-0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,17,1,"j","j",-1.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,18,1,"j","j",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,19,1,"j","j",-2.1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,20,1,"j","j",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,21,1,"j","j",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,22,1,"j","j",-1.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,23,1,"j","j",-1.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,5,26,24,1,"j","j",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,1,1,"j","n",-2.1,null,null,16,null,null,{"$f":"IF(($L646-$I646)/(($C$4-$C$16))>=O$21,1*$F646,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,2,1,"j","n",-2.2000000000000002,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,3,1,"j","n",-2.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,4,1,"j","n",-2.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,5,1,"j","n",-2.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,6,1,"j","n",-2.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,7,1,"j","n",-2.2999999999999998,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,8,1,"j","n",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,9,1,"j","n",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,10,1,"j","n",-1.1000000000000001,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,11,1,"j","n",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,12,1,"j","n",-0.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,13,1,"j","n",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,14,1,"j","n",-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,15,1,"j","n",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,16,1,"j","n",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,17,1,"j","n",-0.4,null,null,{"$f":"IF(AND(H662=\"j\",OR(AND($C$9<=E662,E662<$C$10),AND($D$9<=E662,E662<$D$10))),$J$5,$C$5)*F662","v":16},null,null,{"$f":"IF(($L662-$I662)/(($C$4-$C$16))>=O$21,1*$F662,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,18,{"$f":"IF(AND(B663>$D$13,B663<$I$13),0,IF(B663=$D$13,IF(D663>=$D$12,0,1),IF(B663=$I$13,IF(D663<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C663=7),AND($I$9=1,C663>5)),\"n\",IF($I$9=2,G663,\"j\"))","v":"n"},-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,19,1,"j","n",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,20,1,"j","n",-1.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,21,1,"j","n",-1.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,22,1,"j","n",-2.1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,6,27,23,1,"j","n",-3.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,6,27,24,1,"j","n",-4.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,1,1,"j","n",-3.2,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,2,1,"j","n",-3.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,3,1,"j","n",-4.2,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,4,1,"j","n",-4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,5,1,"j","n",-3.7,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,6,1,"j","n",-3.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,7,1,"j","n",-3.6,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,8,1,"j","n",-3.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,9,1,"j","n",-4.3,null,null,16,null,null,{"$f":"IF(($L678-$I678)/(($C$4-$C$16))>=O$21,1*$F678,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,10,1,"j","n",-4.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,11,1,"j","n",-4.0999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,12,1,"j","n",-3.8,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,13,1,"j","n",-3.4,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,14,1,"j","n",-3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,15,1,"j","n",-2.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,28,16,1,"j","n",-2.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,28,17,1,"j","n",-2.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,28,18,1,"j","n",-2.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,7,28,19,1,"j","n",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,20,1,"j","n",-3.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,21,1,"j","n",-3.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,22,1,"j","n",-3.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,23,1,"j","n",-3.1,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,1,7,28,24,1,"j","n",-2.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,1,1,"j","j",-2.1,null,null,16,null,null,{"$f":"IF(($L694-$I694)/(($C$4-$C$16))>=O$21,1*$F694,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,2,1,"j","j",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,3,1,"j","j",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,4,1,"j","j",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,5,1,"j","j",-1.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,6,1,"j","j",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,7,1,"j","j",-1.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,8,1,"j","j",-1.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,9,1,"j","j",-1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,10,1,"j","j",-0.6,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,11,1,"j","j",-0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,12,1,"j","j",0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,13,1,"j","j",0.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,14,1,"j","j",0.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,29,15,1,"j","j",1.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,29,16,1,"j","j",2.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,29,17,1,"j","j",2.5,null,null,17,null,null,{"$f":"IF(($L710-$I710)/(($C$4-$C$16))>=O$21,1*$F710,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,1,29,18,1,"j","j",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,29,19,1,"j","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,29,20,1,"j","j",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,1,1,29,21,1,"j","j",0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,29,22,1,"j","j",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,29,23,1,"j","j",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,1,29,24,1,"j","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,1,1,"j","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,2,1,"j","j",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,3,1,"j","j",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,4,1,"j","j",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,5,1,"j","j",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,6,1,"j","j",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,7,1,"j","j",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,8,1,"j","j",1.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,9,1,"j","j",1.8,null,null,{"$f":"IF(AND(H726=\"j\",OR(AND($C$9<=E726,E726<$C$10),AND($D$9<=E726,E726<$D$10))),$J$5,$C$5)*F726","v":17},null,null,{"$f":"IF(($L726-$I726)/(($C$4-$C$16))>=O$21,1*$F726,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,10,{"$f":"IF(AND(B727>$D$13,B727<$I$13),0,IF(B727=$D$13,IF(D727>=$D$12,0,1),IF(B727=$I$13,IF(D727<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C727=7),AND($I$9=1,C727>5)),\"n\",IF($I$9=2,G727,\"j\"))","v":"j"},2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,11,1,"j","j",2.2000000000000002,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,12,1,"j","j",2.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,13,1,"j","j",3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,14,1,"j","j",3.3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,1,2,30,15,1,"j","j",3.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,30,16,1,"j","j",3.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,30,17,1,"j","j",3.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,30,18,1,"j","j",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,30,19,1,"j","j",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,30,20,1,"j","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,30,21,1,"j","j",4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,30,22,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,30,23,1,"j","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,2,30,24,1,"j","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,1,1,"j","j",3.7,null,null,16,null,null,{"$f":"IF(($L742-$I742)/(($C$4-$C$16))>=O$21,1*$F742,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,2,1,"j","j",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,3,1,"j","j",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,4,1,"j","j",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,5,1,"j","j",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,6,1,"j","j",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,31,7,1,"j","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,1,3,31,8,1,"j","j",5.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,9,1,"j","j",5.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,10,1,"j","j",5.7,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,11,1,"j","j",5.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,12,1,"j","j",5.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,13,1,"j","j",5.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,14,1,"j","j",6.1,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,15,1,"j","j",6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,16,1,"j","j",5.7,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,17,1,"j","j",5.3,null,null,17,null,null,{"$f":"IF(($L758-$I758)/(($C$4-$C$16))>=O$21,1*$F758,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,18,1,"j","j",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,19,1,"j","j",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,20,1,"j","j",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,21,1,"j","j",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,22,1,"j","j",4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,23,1,"j","j",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,1,3,31,24,1,"j","j",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,1,1,"j","j",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,2,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,3,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,4,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,5,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,6,1,"j","j",4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,7,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,8,1,"j","j",4.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,9,1,"j","j",4.5,null,null,17,null,null,{"$f":"IF(($L774-$I774)/(($C$4-$C$16))>=O$21,1*$F774,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,10,1,"j","j",4.9000000000000004,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,11,1,"j","j",5.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,12,1,"j","j",5.4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,13,1,"j","j",5.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,14,1,"j","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,15,1,"j","j",6.1,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,16,1,"j","j",6.3,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,1,17,1,"j","j",6.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,18,1,"j","j",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,1,19,1,"j","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,4,1,20,1,"j","j",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,21,1,"j","j",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,22,1,"j","j",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,23,1,"j","j",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,1,24,1,"j","j",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,1,1,"j","j",4.2,null,null,{"$f":"IF(AND(H790=\"j\",OR(AND($C$9<=E790,E790<$C$10),AND($D$9<=E790,E790<$D$10))),$J$5,$C$5)*F790","v":16},null,null,{"$f":"IF(($L790-$I790)/(($C$4-$C$16))>=O$21,1*$F790,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,2,{"$f":"IF(AND(B791>$D$13,B791<$I$13),0,IF(B791=$D$13,IF(D791>=$D$12,0,1),IF(B791=$I$13,IF(D791<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C791=7),AND($I$9=1,C791>5)),\"n\",IF($I$9=2,G791,\"j\"))","v":"j"},4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,3,1,"j","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,4,1,"j","j",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,5,1,"j","j",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,6,1,"j","j",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,7,1,"j","j",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,8,1,"j","j",2.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,9,1,"j","j",2.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,10,1,"j","j",2.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,11,1,"j","j",3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,12,1,"j","j",3.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,13,1,"j","j",3.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,14,1,"j","j",4.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,15,1,"j","j",5.0999999999999996,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,16,1,"j","j",5.6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,17,1,"j","j",5.4,null,null,17,null,null,{"$f":"IF(($L806-$I806)/(($C$4-$C$16))>=O$21,1*$F806,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,18,1,"j","j",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,19,1,"j","j",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,20,1,"j","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,2,21,1,"j","j",2.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,22,1,"j","j",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,23,1,"j","j",1.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,2,24,1,"j","j",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,1,1,"j","n",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,2,1,"j","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,3,1,"j","n",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,4,1,"j","n",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,5,1,"j","n",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,6,1,"j","n",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,7,1,"j","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,8,1,"j","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,9,1,"j","n",1.2,null,null,16,null,null,{"$f":"IF(($L822-$I822)/(($C$4-$C$16))>=O$21,1*$F822,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,10,1,"j","n",1.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,11,1,"j","n",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,12,1,"j","n",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,13,1,"j","n",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,14,1,"j","n",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,15,1,"j","n",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,6,3,16,1,"j","n",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,17,1,"j","n",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,18,1,"j","n",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,3,19,1,"j","n",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,20,1,"j","n",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,21,1,"j","n",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,22,1,"j","n",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,23,1,"j","n",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,3,24,1,"j","n",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,7,4,1,1,"j","n",-1.1000000000000001,null,null,16,null,null,{"$f":"IF(($L838-$I838)/(($C$4-$C$16))>=O$21,1*$F838,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,2,7,4,2,1,"j","n",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,7,4,3,1,"j","n",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,4,1,"j","n",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,5,1,"j","n",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,6,1,"j","n",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,7,4,7,1,"j","n",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,7,4,8,1,"j","n",-1.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,7,4,9,1,"j","n",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,7,4,10,1,"j","n",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,7,4,11,1,"j","n",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,12,1,"j","n",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,13,1,"j","n",2.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,14,1,"j","n",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,15,1,"j","n",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,4,16,1,"j","n",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,17,1,"j","n",1.9,null,null,{"$f":"IF(AND(H854=\"j\",OR(AND($C$9<=E854,E854<$C$10),AND($D$9<=E854,E854<$D$10))),$J$5,$C$5)*F854","v":16},null,null,{"$f":"IF(($L854-$I854)/(($C$4-$C$16))>=O$21,1*$F854,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,18,{"$f":"IF(AND(B855>$D$13,B855<$I$13),0,IF(B855=$D$13,IF(D855>=$D$12,0,1),IF(B855=$I$13,IF(D855<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C855=7),AND($I$9=1,C855>5)),\"n\",IF($I$9=2,G855,\"j\"))","v":"n"},1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,19,1,"j","n",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,20,1,"j","n",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,21,1,"j","n",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,22,1,"j","n",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,23,1,"j","n",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,4,24,1,"j","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,1,1,"j","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,2,1,"j","j",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,3,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,4,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,5,1,"j","j",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,6,1,"j","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,7,1,"j","j",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,8,1,"j","j",1.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,9,1,"j","j",1.1000000000000001,null,null,17,null,null,{"$f":"IF(($L870-$I870)/(($C$4-$C$16))>=O$21,1*$F870,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,10,1,"j","j",0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,1,5,11,1,"j","j",0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,1,5,12,1,"j","j",0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,1,5,13,1,"j","j",0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,1,5,14,1,"j","j",0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,1,5,15,1,"j","j",0.6,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,1,5,16,1,"j","j",0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,1,5,17,1,"j","j",0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,1,5,18,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,19,1,"j","j",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,20,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,21,1,"j","j",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,22,1,"j","j",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,23,1,"j","j",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,5,24,1,"j","j",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,6,1,1,"j","j",-0.1,null,null,16,null,null,{"$f":"IF(($L886-$I886)/(($C$4-$C$16))>=O$21,1*$F886,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,2,6,2,1,"j","j",0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,2,6,3,1,"j","j",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,2,6,4,1,"j","j",1.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,2,6,5,1,"j","j",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,2,6,6,1,"j","j",2.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,7,1,"j","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,6,8,1,"j","j",2.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,2,6,9,1,"j","j",2.2999999999999998,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,2,6,10,1,"j","j",1.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,2,6,11,1,"j","j",1.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,2,6,12,1,"j","j",0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,6,13,1,"j","j",0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,6,14,1,"j","j",-0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,6,15,1,"j","j",-0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,6,16,1,"j","j",-1.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,6,17,1,"j","j",-1.4,null,null,17,null,null,{"$f":"IF(($L902-$I902)/(($C$4-$C$16))>=O$21,1*$F902,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,2,2,6,18,1,"j","j",-1.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,6,19,1,"j","j",-1.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,6,20,1,"j","j",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,6,21,1,"j","j",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,6,22,1,"j","j",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,6,23,1,"j","j",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,6,24,1,"j","j",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,1,1,"j","j",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,2,1,"j","j",-1.1000000000000001,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,3,1,"j","j",-0.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,4,1,"j","j",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,5,1,"j","j",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,6,1,"j","j",-0.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,7,1,"j","j",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,8,1,"j","j",-1.1000000000000001,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,9,1,"j","j",-1,null,null,{"$f":"IF(AND(H918=\"j\",OR(AND($C$9<=E918,E918<$C$10),AND($D$9<=E918,E918<$D$10))),$J$5,$C$5)*F918","v":17},null,null,{"$f":"IF(($L918-$I918)/(($C$4-$C$16))>=O$21,1*$F918,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,10,{"$f":"IF(AND(B919>$D$13,B919<$I$13),0,IF(B919=$D$13,IF(D919>=$D$12,0,1),IF(B919=$I$13,IF(D919<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C919=7),AND($I$9=1,C919>5)),\"n\",IF($I$9=2,G919,\"j\"))","v":"j"},-0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,11,1,"j","j",-0.6,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,12,1,"j","j",-0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,13,1,"j","j",-0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,14,1,"j","j",-0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,15,1,"j","j",-0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,16,1,"j","j",-0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,17,1,"j","j",-0.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,18,1,"j","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,19,1,"j","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,20,1,"j","j",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,21,1,"j","j",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,22,1,"j","j",-0.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,23,1,"j","j",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,7,24,1,"j","j",-1.1000000000000001,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,1,1,"j","j",-1.1000000000000001,null,null,16,null,null,{"$f":"IF(($L934-$I934)/(($C$4-$C$16))>=O$21,1*$F934,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,2,1,"j","j",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,3,1,"j","j",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,4,1,"j","j",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,5,1,"j","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,6,1,"j","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,7,1,"j","j",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,8,1,"j","j",-0.9,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,9,1,"j","j",-1.1000000000000001,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,10,1,"j","j",-1.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,11,1,"j","j",-1.1000000000000001,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,12,1,"j","j",-0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,13,1,"j","j",-0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,14,1,"j","j",-0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,15,1,"j","j",-0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,16,1,"j","j",-0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,17,1,"j","j",-0.4,null,null,17,null,null,{"$f":"IF(($L950-$I950)/(($C$4-$C$16))>=O$21,1*$F950,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,18,1,"j","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,19,1,"j","j",-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,8,20,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,8,21,1,"j","j",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,8,22,1,"j","j",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,8,23,1,"j","j",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,8,24,1,"j","j",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,1,1,"j","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,2,1,"j","j",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,3,1,"j","j",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,4,1,"j","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,5,1,"j","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,6,1,"j","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,7,1,"j","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,8,1,"j","j",5.5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,9,1,"j","j",5.6,null,null,17,null,null,{"$f":"IF(($L966-$I966)/(($C$4-$C$16))>=O$21,1*$F966,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,10,1,"j","j",5.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,11,1,"j","j",6.1,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,12,1,"j","j",6.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,13,1,"j","j",6.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,14,1,"j","j",6.8,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,15,1,"j","j",6.9,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,16,1,"j","j",6.8,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,17,1,"j","j",6.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,18,1,"j","j",6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,19,1,"j","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,5,9,20,1,"j","j",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,21,1,"j","j",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,22,1,"j","j",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,23,1,"j","j",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,9,24,1,"j","j",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,1,1,"j","n",5.0999999999999996,null,null,{"$f":"IF(AND(H982=\"j\",OR(AND($C$9<=E982,E982<$C$10),AND($D$9<=E982,E982<$D$10))),$J$5,$C$5)*F982","v":16},null,null,{"$f":"IF(($L982-$I982)/(($C$4-$C$16))>=O$21,1*$F982,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,2,{"$f":"IF(AND(B983>$D$13,B983<$I$13),0,IF(B983=$D$13,IF(D983>=$D$12,0,1),IF(B983=$I$13,IF(D983<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C983=7),AND($I$9=1,C983>5)),\"n\",IF($I$9=2,G983,\"j\"))","v":"n"},5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,3,1,"j","n",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,4,1,"j","n",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,5,1,"j","n",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,6,1,"j","n",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,7,1,"j","n",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,8,1,"j","n",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,9,1,"j","n",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,10,1,"j","n",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,11,1,"j","n",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,12,1,"j","n",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,10,13,1,"j","n",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,6,10,14,1,"j","n",6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,6,10,15,1,"j","n",7.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,6,10,16,1,"j","n",7.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,6,10,17,1,"j","n",8.1,null,null,16,null,null,{"$f":"IF(($L998-$I998)/(($C$4-$C$16))>=O$21,1*$F998,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,2,6,10,18,1,"j","n",8.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,6,10,19,1,"j","n",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,6,10,24,1,"j","n",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,7,11,5,1,"j","n",7.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,7,11,14,1,"j","n",6.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,7,11,22,1,"j","n",9.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,1,12,4,1,"j","j",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,1,12,15,1,"j","j",6.1,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,1,12,18,{"$f":"IF(AND(B1047>$D$13,B1047<$I$13),0,IF(B1047=$D$13,IF(D1047>=$D$12,0,1),IF(B1047=$I$13,IF(D1047<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C1047=7),AND($I$9=1,C1047>5)),\"n\",IF($I$9=2,G1047,\"j\"))","v":"j"},5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,1,12,24,1,"j","j",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,2,13,8,1,"j","j",1.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,2,13,17,1,"j","j",6.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,2,3,14,1,1,"j","j",3.9,null,null,16,null,null,{"$f":"IF(($L1078-$I1078)/(($C$4-$C$16))>=O$21,1*$F1078,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,2,3,14,10,1,"j","j",0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,14,15,1,"j","j",3.1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,15,3,1,"j","j",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,15,5,1,"j","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,4,15,12,1,"j","j",2.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,15,21,1,"j","j",2.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,16,4,1,"j","j",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,16,14,1,"j","j",5.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,17,1,1,"j","n",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,17,7,1,"j","n",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,6,17,15,1,"j","n",9.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,2,6,17,24,1,"j","n",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,7,18,1,1,"j","n",2.5,null,null,{"$f":"IF(AND(H1174=\"j\",OR(AND($C$9<=E1174,E1174<$C$10),AND($D$9<=E1174,E1174<$D$10))),$J$5,$C$5)*F1174","v":16},null,null,{"$f":"IF(($L1174-$I1174)/(($C$4-$C$16))>=O$21,1*$F1174,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,2,7,18,9,1,"j","n",-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,7,18,22,1,"j","n",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,19,2,1,"j","j",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,1,19,12,1,"j","j",0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,1,19,19,1,"j","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,2,20,2,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,2,20,12,1,"j","j",-1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,20,13,1,"j","j",-0.9,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,21,1,1,"j","j",-3.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,2,3,21,6,1,"j","j",-2.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,3,21,18,1,"j","j",2.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,3,21,23,1,"j","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,22,8,1,"j","j",1.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,4,22,16,1,"j","j",4.0999999999999996,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,4,22,22,1,"j","j",4.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,2,5,23,1,1,"j","j",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,23,12,1,"j","j",1.3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,5,23,18,1,"j","j",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,24,2,1,"j","n",0.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,6,24,11,1,"j","n",-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,6,24,19,1,"j","n",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,25,4,1,"j","n",-2.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,7,25,13,1,"j","n",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,25,18,1,"j","n",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,2,7,25,22,1,"j","n",-1.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,1,26,8,1,"n","j",-4.0999999999999996,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,2,1,26,15,1,"n","j",0,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,1,26,22,1,"n","j",-2.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,2,2,27,8,1,"n","j",-3.7,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,2,2,27,12,1,"n","j",-2.2999999999999998,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,2,3,28,1,1,"n","j",-3.6,null,null,16,null,null,{"$f":"IF(($L1414-$I1414)/(($C$4-$C$16))>=O$21,1*$F1414,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,2,3,28,2,1,"n","j",-3.8,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,2,3,28,10,1,"n","j",-3.6,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,2,3,28,19,1,"n","j",-1.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,4,1,3,1,"n","j",-1.1000000000000001,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,4,1,9,1,"n","j",-1.4,null,null,17,null,null,{"$f":"IF(($L1446-$I1446)/(($C$4-$C$16))>=O$21,1*$F1446,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,3,4,1,20,1,"n","j",-1.1000000000000001,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,5,2,5,1,"n","j",-2.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,5,2,8,1,"n","j",-2.2000000000000002,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,3,5,2,14,1,"n","j",1.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,5,2,22,1,"n","j",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,6,3,7,1,"n","n",0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,6,3,19,1,"n","n",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,6,3,24,1,"n","n",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,7,4,5,1,"n","n",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,7,4,17,1,"n","n",6.9,null,null,16,null,null,{"$f":"IF(($L1526-$I1526)/(($C$4-$C$16))>=O$21,1*$F1526,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,3,7,4,19,1,"n","n",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,1,5,2,1,"j","j",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,1,5,16,1,"j","j",6.3,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,1,5,19,1,"j","j",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,2,6,6,1,"j","j",-2.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,2,6,12,1,"j","j",3.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,2,6,21,1,"j","j",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,3,7,5,1,"j","j",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,3,7,14,1,"j","j",7.1,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,3,7,19,1,"j","j",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,3,7,23,1,"j","j",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,4,8,12,1,"j","j",5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,4,8,16,1,"j","j",8.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,5,9,2,1,"j","j",-0.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,5,9,9,1,"j","j",1.1000000000000001,null,null,17,null,null,{"$f":"IF(($L1638-$I1638)/(($C$4-$C$16))>=O$21,1*$F1638,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,3,5,9,16,1,"j","j",9.3000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,6,10,2,1,"j","n",-0.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,6,10,6,1,"j","n",-1.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,6,10,11,1,"j","n",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,6,10,23,1,"j","n",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,7,11,4,1,"j","n",5.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,7,11,13,1,"j","n",6.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,7,11,19,1,"j","n",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,1,12,6,1,"j","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,1,12,12,1,"j","j",7.5,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,1,12,15,1,"j","j",7.3,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,2,13,2,1,"j","j",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,2,13,8,1,"j","j",7,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,2,13,16,1,"j","j",9.9,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,3,14,1,1,"j","j",7.2,null,null,{"$f":"IF(AND(H1750=\"j\",OR(AND($C$9<=E1750,E1750<$C$10),AND($D$9<=E1750,E1750<$D$10))),$J$5,$C$5)*F1750","v":16},null,null,{"$f":"IF(($L1750-$I1750)/(($C$4-$C$16))>=O$21,1*$F1750,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,3,3,14,6,1,"j","j",7.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,3,14,18,1,"j","j",8.6999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,3,3,14,23,1,"j","j",6.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,4,15,3,1,"j","j",6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,4,15,13,1,"j","j",8.1999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,4,15,20,1,"j","j",4.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,5,16,5,1,"j","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,5,16,12,1,"j","j",2.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,5,16,22,1,"j","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,6,17,2,1,"j","n",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,6,17,15,1,"j","n",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,6,17,16,1,"j","n",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,6,17,24,1,"j","n",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,7,18,13,1,"j","n",6.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,7,18,17,1,"j","n",7.6,null,null,16,null,null,{"$f":"IF(($L1862-$I1862)/(($C$4-$C$16))>=O$21,1*$F1862,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,3,7,18,23,1,"j","n",6.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,1,19,10,{"$f":"IF(AND(B1879>$D$13,B1879<$I$13),0,IF(B1879=$D$13,IF(D1879>=$D$12,0,1),IF(B1879=$I$13,IF(D1879<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C1879=7),AND($I$9=1,C1879>5)),\"n\",IF($I$9=2,G1879,\"j\"))","v":"j"},4.4000000000000004,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,1,19,13,1,"j","j",6,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,2,20,3,1,"j","j",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,2,20,10,1,"j","j",3.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,2,20,12,1,"j","j",3.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,2,20,21,1,"j","j",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,3,21,9,1,"j","j",0.2,null,null,17,null,null,{"$f":"IF(($L1926-$I1926)/(($C$4-$C$16))>=O$21,1*$F1926,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,3,3,21,14,1,"j","j",4.5999999999999996,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,3,21,23,1,"j","j",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,4,22,7,1,"j","j",-3.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,3,4,22,13,1,"j","j",1.6,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,4,22,16,1,"j","j",2.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,5,23,6,1,"j","j",-5.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,3,5,23,9,1,"j","j",-3.2,null,null,17,null,null,{"$f":"IF(($L1974-$I1974)/(($C$4-$C$16))>=O$21,1*$F1974,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,3,5,23,20,1,"j","j",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,6,24,2,1,"j","n",-2.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,6,24,10,1,"j","n",-3.1,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,3,6,24,19,1,"j","n",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,6,24,24,1,"j","n",-1.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,7,25,4,1,"j","n",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,7,25,13,1,"j","n",-1.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,7,25,23,1,"j","n",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,1,26,6,1,"j","j",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,1,26,13,1,"j","j",-1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,1,26,23,1,"j","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,2,27,6,1,"j","j",-2.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,2,27,16,1,"j","j",1.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,2,27,20,1,"j","j",-1.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,3,28,1,1,"j","j",-3.6,null,null,16,null,null,{"$f":"IF(($L2086-$I2086)/(($C$4-$C$16))>=O$21,1*$F2086,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,3,3,28,10,1,"j","j",-2.7,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,3,3,28,18,1,"j","j",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,3,28,24,1,"j","j",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,4,29,11,1,"j","j",-0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,4,29,17,1,"j","j",2.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,5,30,4,1,"j","j",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,5,30,5,1,"j","j",-0.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,3,5,30,13,1,"j","j",1.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,3,5,30,22,1,"j","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,6,31,6,1,"j","n",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,3,6,31,15,1,"j","n",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,3,6,31,20,1,"j","n",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,7,1,8,1,"j","n",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,7,1,10,1,"j","n",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,7,1,17,1,"j","n",3.9,null,null,{"$f":"IF(AND(H2198=\"j\",OR(AND($C$9<=E2198,E2198<$C$10),AND($D$9<=E2198,E2198<$D$10))),$J$5,$C$5)*F2198","v":16},null,null,{"$f":"IF(($L2198-$I2198)/(($C$4-$C$16))>=O$21,1*$F2198,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,4,1,2,7,1,"n","j",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,1,2,10,1,"n","j",2.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,1,2,17,1,"n","j",2.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,2,3,3,1,"n","j",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,4,2,3,7,1,"n","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,4,2,3,20,1,"n","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,3,4,5,1,"n","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,4,3,4,6,1,"n","j",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,4,3,4,14,1,"n","j",0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,4,4,5,3,1,"n","j",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,4,4,5,7,1,"n","j",-1.1000000000000001,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,4,4,5,17,1,"n","j",0.6,null,null,17,null,null,{"$f":"IF(($L2294-$I2294)/(($C$4-$C$16))>=O$21,1*$F2294,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,4,4,5,24,1,"n","j",-2.2000000000000002,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,4,5,6,7,1,"n","j",-2.2999999999999998,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,4,5,6,17,1,"n","j",1.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,5,6,24,1,"n","j",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,4,6,7,2,{"$f":"IF(AND(B2327>$D$13,B2327<$I$13),0,IF(B2327=$D$13,IF(D2327>=$D$12,0,1),IF(B2327=$I$13,IF(D2327<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C2327=7),AND($I$9=1,C2327>5)),\"n\",IF($I$9=2,G2327,\"j\"))","v":"n"},-1.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,4,6,7,14,1,"n","n",6.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,6,7,19,1,"n","n",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,7,8,4,1,"n","n",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,7,8,12,1,"n","n",5.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,7,8,21,1,"n","n",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,1,9,3,1,"n","j",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,1,9,6,1,"n","j",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,1,9,17,1,"n","j",12.6,null,null,{"$f":"IF(AND(H2390=\"j\",OR(AND($C$9<=E2390,E2390<$C$10),AND($D$9<=E2390,E2390<$D$10))),$J$5,$C$5)*F2390","v":17},null,null,{"$f":"IF(($L2390-$I2390)/(($C$4-$C$16))>=O$21,1*$F2390,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,4,1,9,23,1,"n","j",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,2,10,7,1,"n","j",5.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,2,10,16,1,"n","j",15.9,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,4,2,10,24,1,"n","j",9.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,3,11,9,1,"n","j",8.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,3,11,14,1,"n","j",9.4,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,3,11,18,1,"n","j",7.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,4,12,4,1,"n","j",6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,4,12,11,1,"n","j",8.3000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,4,12,18,1,"n","j",11.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,4,5,13,4,1,"n","j",6.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,5,13,13,1,"n","j",14.1,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,4,5,13,17,1,"n","j",15.4,null,null,17,null,null,{"$f":"IF(($L2486-$I2486)/(($C$4-$C$16))>=O$21,1*$F2486,0)","v":0},0,0,0,0,0,0,0,0,0,1]
[null,4,6,14,6,1,"n","n",7.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,6,14,7,1,"n","n",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,6,14,15,1,"n","n",15.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,4,6,14,24,1,"n","n",11.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,4,7,15,8,1,"n","n",9.8000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,7,15,14,1,"n","n",16.5,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,4,1,16,1,1,"j","j",11.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,4,1,16,4,1,"j","j",9.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,4,1,16,18,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,2,17,1,1,"j","j",0.8,null,null,16,null,null,{"$f":"IF(($L2566-$I2566)/(($C$4-$C$16))>=O$21,1*$F2566,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,4,2,17,3,1,"j","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,2,17,11,1,"j","j",1.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,2,17,20,1,"j","j",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,3,18,1,1,"j","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,3,18,13,1,"j","j",1.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,3,18,22,1,"j","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,3,18,24,1,"j","j",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,4,4,19,7,1,"j","j",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,4,4,19,21,1,"j","j",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,4,19,24,1,"j","j",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,5,20,11,1,"j","j",4.4000000000000004,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,5,20,17,1,"j","j",5.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,6,21,1,1,"j","n",3.3,null,null,16,null,null,{"$f":"IF(($L2662-$I2662)/(($C$4-$C$16))>=O$21,1*$F2662,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,4,6,21,10,1,"j","n",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,6,21,18,1,"j","n",5.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,6,21,19,1,"j","n",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,7,22,8,1,"j","n",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,7,22,12,1,"j","n",5.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,7,22,22,1,"j","n",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,1,23,5,1,"j","j",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,1,23,14,1,"j","j",8.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,1,23,21,1,"j","j",5.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,2,24,7,1,"j","j",2.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,2,24,11,1,"j","j",3.1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,2,24,16,1,"j","j",5.5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,3,25,4,1,"j","j",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,3,25,9,1,"j","j",2.2000000000000002,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,3,25,18,{"$f":"IF(AND(B2775>$D$13,B2775<$I$13),0,IF(B2775=$D$13,IF(D2775>=$D$12,0,1),IF(B2775=$I$13,IF(D2775<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C2775=7),AND($I$9=1,C2775>5)),\"n\",IF($I$9=2,G2775,\"j\"))","v":"j"},2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,4,26,2,1,"j","j",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,4,26,8,1,"j","j",1.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,4,26,19,1,"j","j",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,4,26,22,1,"j","j",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,5,27,4,1,"j","j",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,5,27,12,1,"j","j",3.1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,5,27,21,1,"j","j",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,6,28,6,1,"j","n",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,6,28,11,1,"j","n",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,6,28,23,1,"j","n",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,7,29,4,1,"j","n",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,7,29,8,1,"j","n",2.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,4,7,29,18,1,"j","n",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,4,1,30,1,1,"j","j",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,1,30,8,1,"j","j",4.9000000000000004,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,1,30,18,1,"j","j",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,4,1,30,22,1,"j","j",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,5,2,1,11,1,"j","j",6.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,5,2,1,19,1,"j","j",7.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,2,1,20,1,"j","j",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,3,2,5,1,"j","j",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,3,2,13,1,"j","j",16.399999999999999,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,3,2,22,1,"j","j",15.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,4,3,4,1,"j","j",11.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,4,3,15,1,"j","j",16.3,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,4,3,18,{"$f":"IF(AND(B2967>$D$13,B2967<$I$13),0,IF(B2967=$D$13,IF(D2967>=$D$12,0,1),IF(B2967=$I$13,IF(D2967<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C2967=7),AND($I$9=1,C2967>5)),\"n\",IF($I$9=2,G2967,\"j\"))","v":"j"},16.100000000000001,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,5,4,8,1,"j","j",9.5,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,5,4,15,1,"j","j",13.3,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,5,4,17,1,"j","j",11.9,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,6,5,5,1,"j","n",7.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,6,5,10,1,"j","n",12.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,6,5,15,1,"j","n",16,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,7,6,3,1,"j","n",10.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,7,6,12,1,"j","n",7.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,7,6,20,1,"j","n",7.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,1,7,2,1,"j","j",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,5,1,7,5,1,"j","j",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,5,1,7,14,1,"j","j",12,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,2,8,1,1,"j","j",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,2,8,7,1,"j","j",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,2,8,15,1,"j","j",11.7,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,2,8,24,1,"j","j",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,3,9,5,1,"j","j",6.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,3,9,9,1,"j","j",9.6,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,3,9,22,1,"j","j",5.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,5,4,10,2,1,"j","j",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,5,4,10,12,1,"j","j",10.6,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,4,10,19,1,"j","j",9.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,5,5,11,2,1,"j","j",11,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,5,11,12,1,"j","j",15,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,5,11,16,1,"j","j",15.7,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,5,11,21,1,"j","j",13.9,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,6,12,6,1,"j","n",11.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,5,6,12,15,1,"j","n",22.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,12,23,1,"j","n",15.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,7,13,5,1,"j","n",16,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,5,7,13,16,1,"j","n",25.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,7,13,22,1,"j","n",20,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,1,14,9,1,"j","j",20.9,null,null,{"$f":"IF(AND(H3222=\"j\",OR(AND($C$9<=E3222,E3222<$C$10),AND($D$9<=E3222,E3222<$D$10))),$J$5,$C$5)*F3222","v":17},null,null,{"$f":"IF(($L3222-$I3222)/(($C$4-$C$16))>=O$21,1*$F3222,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,5,1,14,12,1,"j","j",25.1,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,1,14,18,1,"j","j",21.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,15,2,0,"j","j",9.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,15,11,0,"j","j",11.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,15,16,0,"j","j",15.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,16,4,0,"j","j",9.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,16,9,0,"j","j",7.7,null,null,0,null,null,{"$f":"IF(($L3270-$I3270)/(($C$4-$C$16))>=O$21,1*$F3270,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,5,3,16,21,0,"j","j",6.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,16,22,0,"j","j",6.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,17,12,0,"j","j",9.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,17,15,0,"j","j",10.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,17,22,0,"j","j",8.8000000000000007,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,5,18,8,0,"j","j",5.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,5,18,12,0,"j","j",6.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,19,1,0,"j","n",1.7,null,null,0,null,null,{"$f":"IF(($L3334-$I3334)/(($C$4-$C$16))>=O$21,1*$F3334,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,5,6,19,9,0,"j","n",2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,19,10,0,"j","n",3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,19,23,0,"j","n",2.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,7,20,3,0,"j","n",0.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,7,20,9,0,"j","n",3.5,null,null,0,null,null,{"$f":"IF(($L3366-$I3366)/(($C$4-$C$16))>=O$21,1*$F3366,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,5,7,20,20,0,"j","n",6.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,1,21,6,0,"j","j",3.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,1,21,13,0,"j","j",11.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,1,21,22,0,"j","j",8.6999999999999993,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,22,5,0,"j","j",5.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,22,7,0,"j","j",7.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,22,19,0,"j","j",12.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,22,24,0,"j","j",6.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,23,9,0,"j","j",9.3000000000000007,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,23,17,0,"j","j",17.5,null,null,0,null,null,{"$f":"IF(($L3446-$I3446)/(($C$4-$C$16))>=O$21,1*$F3446,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,5,3,23,23,0,"j","j",12.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,24,10,0,"j","j",17,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,24,16,0,"j","j",20.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,24,19,0,"j","j",17.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,5,25,6,0,"j","j",10.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,5,25,12,0,"j","j",15.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,5,25,20,0,"j","j",11.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,26,5,0,"j","n",8.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,26,14,0,"j","n",9.8000000000000007,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,26,19,0,"j","n",10.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,6,26,23,0,"j","n",5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,7,27,9,0,"j","n",10.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,7,27,16,0,"j","n",12.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,7,27,23,0,"j","n",10.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,1,28,9,0,"j","j",9.6,null,null,0,null,null,{"$f":"IF(($L3558-$I3558)/(($C$4-$C$16))>=O$21,1*$F3558,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,5,1,28,16,0,"j","j",12.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,29,2,0,"j","j",8.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,29,6,0,"j","j",7.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,29,11,0,"j","j",12.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,2,29,20,0,"j","j",14.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,30,4,0,"j","j",8.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,30,10,{"$f":"IF(AND(B3607>$D$13,B3607<$I$13),0,IF(B3607=$D$13,IF(D3607>=$D$12,0,1),IF(B3607=$I$13,IF(D3607<$I$12,0,1),1)))","v":0},"j",{"$f":"IF(OR(AND($I$9=3,C3607=7),AND($I$9=1,C3607>5)),\"n\",IF($I$9=2,G3607,\"j\"))","v":"j"},10.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,3,30,21,0,"j","j",9.6999999999999993,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,31,6,0,"j","j",7.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,31,9,0,"j","j",7.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,5,4,31,23,0,"j","j",8.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,1,6,0,"j","j",11.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,1,8,0,"j","j",14.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,1,16,0,"j","j",19.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,2,1,0,"j","n",13.2,null,null,{"$f":"IF(AND(H3670=\"j\",OR(AND($C$9<=E3670,E3670<$C$10),AND($D$9<=E3670,E3670<$D$10))),$J$5,$C$5)*F3670","v":0},null,null,{"$f":"IF(($L3670-$I3670)/(($C$4-$C$16))>=O$21,1*$F3670,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,6,2,6,0,"j","n",12.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,2,18,0,"j","n",19.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,3,3,0,"j","n",13.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,3,11,0,"j","n",20.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,3,17,0,"j","n",18.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,3,20,0,"j","n",16.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,4,3,0,"j","j",12.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,4,13,0,"j","j",21.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,4,22,0,"j","j",14.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,5,6,0,"j","j",12.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,5,15,0,"j","j",17.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,5,23,0,"j","j",13.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,5,24,0,"j","j",12.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,6,13,0,"j","j",11,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,6,17,0,"j","j",11.6,null,null,0,null,null,{"$f":"IF(($L3782-$I3782)/(($C$4-$C$16))>=O$21,1*$F3782,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,4,7,3,0,"j","j",10.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,7,10,{"$f":"IF(AND(B3799>$D$13,B3799<$I$13),0,IF(B3799=$D$13,IF(D3799>=$D$12,0,1),IF(B3799=$I$13,IF(D3799<$I$12,0,1),1)))","v":0},"j",{"$f":"IF(OR(AND($I$9=3,C3799=7),AND($I$9=1,C3799>5)),\"n\",IF($I$9=2,G3799,\"j\"))","v":"j"},9.6999999999999993,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,7,17,0,"j","j",10.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,8,3,0,"j","j",9.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,8,10,0,"j","j",11.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,8,12,0,"j","j",12.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,8,24,0,"j","j",9.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,9,5,0,"j","n",8.3000000000000007,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,9,14,0,"j","n",13.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,9,23,0,"j","n",10.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,10,7,0,"j","n",11.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,10,13,0,"j","n",11.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,10,24,0,"j","n",8.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,11,3,0,"j","j",8.6999999999999993,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,11,9,0,"j","j",11,null,null,0,null,null,{"$f":"IF(($L3894-$I3894)/(($C$4-$C$16))>=O$21,1*$F3894,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,1,11,17,0,"j","j",13.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,12,2,0,"j","j",8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,12,10,0,"j","j",10.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,12,19,0,"j","j",10.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,12,24,0,"j","j",6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,13,12,0,"j","j",13.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,13,14,0,"j","j",13.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,13,21,0,"j","j",11.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,14,6,0,"j","j",10,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,14,13,0,"j","j",15.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,14,23,0,"j","j",9.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,15,3,0,"j","j",9.6999999999999993,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,15,16,0,"j","j",11,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,15,24,0,"j","j",5.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,16,1,0,"j","n",5,null,null,0,null,null,{"$f":"IF(($L4006-$I4006)/(($C$4-$C$16))>=O$21,1*$F4006,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,6,16,10,0,"j","n",6.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,16,18,0,"j","n",9.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,16,24,0,"j","n",7.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,17,11,0,"j","n",9.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,17,21,0,"j","n",7.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,18,4,0,"j","j",5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,18,11,0,"j","j",7.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,18,13,0,"j","j",9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,18,21,0,"j","j",7.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,19,6,0,"j","j",7.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,19,15,0,"j","j",10.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,19,20,0,"j","j",9.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,20,8,0,"j","j",9.6999999999999993,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,20,17,0,"j","j",13.7,null,null,{"$f":"IF(AND(H4118=\"j\",OR(AND($C$9<=E4118,E4118<$C$10),AND($D$9<=E4118,E4118<$D$10))),$J$5,$C$5)*F4118","v":0},null,null,{"$f":"IF(($L4118-$I4118)/(($C$4-$C$16))>=O$21,1*$F4118,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,4,21,1,0,"j","j",10.199999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,21,7,0,"j","j",8.3000000000000007,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,21,10,0,"j","j",10.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,21,21,0,"j","j",12.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,22,3,0,"j","j",9.1999999999999993,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,22,11,0,"j","j",10.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,22,20,0,"j","j",12.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,23,4,0,"j","n",4.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,23,13,0,"j","n",13.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,23,18,0,"j","n",15.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,23,22,0,"j","n",11.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,24,7,0,"j","n",9.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,7,24,17,0,"j","n",18.7,null,null,0,null,null,{"$f":"IF(($L4214-$I4214)/(($C$4-$C$16))>=O$21,1*$F4214,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,6,7,24,24,0,"j","n",9.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,25,7,0,"j","j",12.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,25,17,0,"j","j",15.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,1,25,21,0,"j","j",15,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,26,2,{"$f":"IF(AND(B4247>$D$13,B4247<$I$13),0,IF(B4247=$D$13,IF(D4247>=$D$12,0,1),IF(B4247=$I$13,IF(D4247<$I$12,0,1),1)))","v":0},"j",{"$f":"IF(OR(AND($I$9=3,C4247=7),AND($I$9=1,C4247>5)),\"n\",IF($I$9=2,G4247,\"j\"))","v":"j"},12.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,26,11,0,"j","j",13.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,2,26,19,0,"j","j",13.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,27,4,0,"j","j",10.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,27,12,0,"j","j",11.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,3,27,18,0,"j","j",12.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,28,5,0,"j","j",9.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,28,8,0,"j","j",9.8000000000000007,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,28,14,0,"j","j",11.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,4,28,23,0,"j","j",7.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,29,7,0,"j","j",6.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,29,16,0,"j","j",12.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,5,29,21,0,"j","j",9.8000000000000007,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,30,9,0,"j","n",9.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,6,6,30,14,0,"j","n",12.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,1,2,0,"n","n",9.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,1,4,0,"n","n",8.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,1,11,0,"n","n",12.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,1,18,0,"n","n",17.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,2,4,0,"n","j",9.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,2,15,0,"n","j",18.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,2,21,0,"n","j",18.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,3,5,0,"n","j",14,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,3,14,0,"n","j",25.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,3,15,0,"n","j",25.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,4,4,0,"n","j",15.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,4,8,0,"n","j",18.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,4,14,0,"n","j",24.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,5,1,0,"n","j",17.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,5,11,0,"n","j",21.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,5,18,0,"n","j",23.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,6,1,0,"n","j",16.2,null,null,0,null,null,{"$f":"IF(($L4486-$I4486)/(($C$4-$C$16))>=O$21,1*$F4486,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,5,6,3,0,"n","j",15.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,6,15,0,"n","j",22.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,6,20,0,"n","j",21.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,7,8,0,"n","n",17.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,7,13,0,"n","n",20.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,7,22,0,"n","n",16.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,8,6,0,"n","n",13.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,8,15,0,"n","n",20.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,8,21,0,"n","n",18,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,8,24,0,"n","n",15.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,9,11,0,"n","j",16.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,9,17,0,"n","j",18.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,10,1,0,"n","j",13.3,null,null,0,null,null,{"$f":"IF(($L4582-$I4582)/(($C$4-$C$16))>=O$21,1*$F4582,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,2,10,10,0,"n","j",17.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,10,15,0,"n","j",21.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,11,3,0,"n","j",14.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,11,8,0,"n","j",17.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,11,12,0,"n","j",21.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,11,22,0,"n","j",18.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,12,5,0,"n","j",17.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,12,12,0,"n","j",23.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,12,22,0,"n","j",20,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,13,7,0,"n","j",16,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,13,11,0,"n","j",18.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,13,16,0,"n","j",17.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,14,1,0,"n","n",12.9,null,null,0,null,null,{"$f":"IF(($L4678-$I4678)/(($C$4-$C$16))>=O$21,1*$F4678,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,6,14,9,0,"n","n",9.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,14,15,0,"n","n",13.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,15,2,0,"n","n",7.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,15,8,0,"n","n",8.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,15,19,0,"n","n",11.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,15,22,0,"n","n",10,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,16,4,0,"n","j",6.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,16,12,0,"n","j",12.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,16,21,0,"n","j",11.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,17,9,0,"n","j",11.6,null,null,{"$f":"IF(AND(H4758=\"j\",OR(AND($C$9<=E4758,E4758<$C$10),AND($D$9<=E4758,E4758<$D$10))),$J$5,$C$5)*F4758","v":0},null,null,{"$f":"IF(($L4758-$I4758)/(($C$4-$C$16))>=O$21,1*$F4758,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,2,17,14,0,"n","j",14.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,17,23,0,"n","j",12.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,18,8,0,"n","j",10.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,18,16,0,"n","j",13,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,18,22,0,"n","j",12.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,19,1,0,"n","j",9.6999999999999993,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,19,8,0,"n","j",9.8000000000000007,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,19,18,0,"n","j",14,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,20,5,0,"n","j",11.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,20,11,0,"n","j",11.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,20,19,0,"n","j",10.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,21,4,0,"n","n",9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,21,9,0,"n","n",11,null,null,0,null,null,{"$f":"IF(($L4854-$I4854)/(($C$4-$C$16))>=O$21,1*$F4854,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,6,21,13,0,"n","n",12.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,22,2,0,"n","n",9.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,22,6,0,"n","n",7.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,22,15,0,"n","n",15.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,22,22,0,"n","n",14,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,23,8,0,"n","j",14,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,23,15,0,"n","j",17.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,23,17,0,"n","j",18.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,24,5,0,"n","j",16.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,24,10,0,"n","j",14.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,24,19,0,"n","j",11.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,25,3,0,"n","j",10.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,3,25,9,0,"n","j",10.4,null,null,{"$f":"IF(AND(H4950=\"j\",OR(AND($C$9<=E4950,E4950<$C$10),AND($D$9<=E4950,E4950<$D$10))),$J$5,$C$5)*F4950","v":0},null,null,{"$f":"IF(($L4950-$I4950)/(($C$4-$C$16))>=O$21,1*$F4950,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,3,25,20,0,"n","j",9.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,26,2,0,"n","j",9.3000000000000007,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,26,5,0,"n","j",9.3000000000000007,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,26,16,0,"n","j",13.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,4,26,22,0,"n","j",9.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,27,7,0,"n","j",8.8000000000000007,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,27,15,0,"n","j",13.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,5,27,24,0,"n","j",10.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,28,5,0,"n","n",9.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,6,28,17,0,"n","n",13.7,null,null,0,null,null,{"$f":"IF(($L5030-$I5030)/(($C$4-$C$16))>=O$21,1*$F5030,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,6,28,19,0,"n","n",13,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,29,2,0,"n","n",11.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,7,29,9,0,"n","n",12.8,null,null,0,null,null,{"$f":"IF(($L5046-$I5046)/(($C$4-$C$16))>=O$21,1*$F5046,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,7,7,29,19,0,"n","n",12.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,30,2,0,"n","j",13.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,30,12,0,"n","j",15.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,1,30,16,0,"n","j",17.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,31,5,0,"n","j",12.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,31,6,0,"n","j",12,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,31,14,0,"n","j",13.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,7,2,31,23,0,"n","j",11.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,1,5,0,"n","j",13.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,1,16,0,"n","j",22.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,2,2,0,"n","j",14.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,2,9,0,"n","j",18.399999999999999,null,null,{"$f":"IF(AND(H5142=\"j\",OR(AND($C$9<=E5142,E5142<$C$10),AND($D$9<=E5142,E5142<$D$10))),$J$5,$C$5)*F5142","v":0},null,null,{"$f":"IF(($L5142-$I5142)/(($C$4-$C$16))>=O$21,1*$F5142,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,4,2,16,0,"n","j",23.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,2,18,0,"n","j",22.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,3,2,0,"n","j",16.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,3,11,0,"n","j",22.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,3,23,0,"n","j",16.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,4,4,0,"n","n",15.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,4,13,0,"n","n",23.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,4,21,0,"n","n",20.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,5,3,0,"n","n",18.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,5,6,0,"n","n",18.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,5,15,0,"n","n",24.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,6,2,0,"n","j",17.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,6,8,0,"n","j",18.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,6,16,0,"n","j",24.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,7,1,0,"n","j",18.3,null,null,0,null,null,{"$f":"IF(($L5254-$I5254)/(($C$4-$C$16))>=O$21,1*$F5254,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,2,7,9,0,"n","j",18.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,7,18,{"$f":"IF(AND(B5271>$D$13,B5271<$I$13),0,IF(B5271=$D$13,IF(D5271>=$D$12,0,1),IF(B5271=$I$13,IF(D5271<$I$12,0,1),1)))","v":0},"n",{"$f":"IF(OR(AND($I$9=3,C5271=7),AND($I$9=1,C5271>5)),\"n\",IF($I$9=2,G5271,\"j\"))","v":"j"},20.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,7,23,0,"n","j",16.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,8,3,0,"n","j",15.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,8,13,0,"n","j",15.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,8,20,0,"n","j",12.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,9,3,0,"n","j",11.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,9,13,0,"n","j",16.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,9,20,0,"n","j",16,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,10,6,0,"n","j",11.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,10,7,0,"n","j",11.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,10,16,0,"n","j",13.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,10,24,0,"n","j",13.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,11,9,0,"n","n",12.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,11,17,0,"n","n",15.7,null,null,0,null,null,{"$f":"IF(($L5366-$I5366)/(($C$4-$C$16))>=O$21,1*$F5366,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,6,11,23,0,"n","n",11.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,12,10,0,"n","n",13,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,12,13,0,"n","n",17.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,12,19,0,"n","n",18.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,13,3,0,"n","j",12.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,13,12,0,"n","j",19.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,13,20,0,"n","j",20.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,14,5,0,"n","j",14.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,14,10,0,"n","j",15,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,14,22,0,"n","j",12.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,15,7,0,"n","j",11.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,15,9,0,"n","j",13.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,15,16,0,"n","j",17.100000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,15,23,0,"n","j",11.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,16,9,0,"n","j",14.4,null,null,0,null,null,{"$f":"IF(($L5478-$I5478)/(($C$4-$C$16))>=O$21,1*$F5478,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,4,16,20,0,"n","j",13.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,17,2,0,"n","j",8.1999999999999993,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,17,10,0,"n","j",9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,17,19,0,"n","j",13.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,17,20,0,"n","j",12,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,18,4,0,"n","n",5.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,18,17,0,"n","n",15,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,18,21,0,"n","n",13.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,19,7,0,"n","n",11.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,19,14,0,"n","n",15.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,19,21,0,"n","n",16.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,20,7,0,"n","j",11.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,20,8,0,"n","j",11.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,20,20,0,"n","j",11.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,21,1,0,"n","j",9.9,null,null,{"$f":"IF(AND(H5590=\"j\",OR(AND($C$9<=E5590,E5590<$C$10),AND($D$9<=E5590,E5590<$D$10))),$J$5,$C$5)*F5590","v":0},null,null,{"$f":"IF(($L5590-$I5590)/(($C$4-$C$16))>=O$21,1*$F5590,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,2,21,13,0,"n","j",13,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,21,18,0,"n","j",12.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,22,3,0,"n","j",8.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,22,11,0,"n","j",12.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,22,17,0,"n","j",13.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,22,20,0,"n","j",11.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,23,7,0,"n","j",8.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,23,13,0,"n","j",15.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,23,21,0,"n","j",12.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,24,6,0,"n","j",11.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,24,14,0,"n","j",17.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,24,23,0,"n","j",12.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,25,8,0,"n","n",12.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,25,13,0,"n","n",19.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,6,25,17,0,"n","n",18,null,null,0,null,null,{"$f":"IF(($L5702-$I5702)/(($C$4-$C$16))>=O$21,1*$F5702,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,7,26,3,0,"n","n",11.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,26,10,{"$f":"IF(AND(B5719>$D$13,B5719<$I$13),0,IF(B5719=$D$13,IF(D5719>=$D$12,0,1),IF(B5719=$I$13,IF(D5719<$I$12,0,1),1)))","v":0},"n",{"$f":"IF(OR(AND($I$9=3,C5719=7),AND($I$9=1,C5719>5)),\"n\",IF($I$9=2,G5719,\"j\"))","v":"n"},17.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,7,26,17,0,"n","n",20.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,27,3,0,"n","j",12,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,27,7,0,"n","j",11.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,27,20,0,"n","j",18,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,1,27,21,0,"n","j",16.399999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,28,5,0,"n","j",11.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,28,14,0,"n","j",21.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,2,28,22,0,"n","j",14.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,29,4,0,"n","j",12.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,29,15,0,"n","j",19.600000000000001,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,3,29,24,0,"n","j",15.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,30,3,0,"n","j",15.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,4,30,9,0,"n","j",16,null,null,0,null,null,{"$f":"IF(($L5814-$I5814)/(($C$4-$C$16))>=O$21,1*$F5814,0)","v":0},0,0,0,0,0,0,0,0,0,0]
[null,8,4,30,17,0,"n","j",21,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,31,2,0,"n","j",13.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,31,14,0,"n","j",18.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,31,19,0,"n","j",16.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,8,5,31,24,0,"n","j",15.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,1,12,0,"j","n",16.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,1,14,0,"j","n",17.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,1,21,0,"j","n",13.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,2,11,0,"j","n",16.899999999999999,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,2,14,0,"j","n",19,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,1,3,1,0,"j","j",13.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,1,3,7,0,"j","j",12.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,1,3,16,0,"j","j",13.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,1,3,24,0,"j","j",11.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,4,9,0,"j","j",10.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,4,14,0,"j","j",17,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,4,18,0,"j","j",16,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,5,7,0,"j","j",11.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,5,11,0,"j","j",15,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,5,21,0,"j","j",12.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,6,4,0,"j","j",11.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,6,11,0,"j","j",17,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,6,21,0,"j","j",15,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,7,1,0,"j","j",15.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,7,6,0,"j","j",15,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,7,15,0,"j","j",14.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,7,23,0,"j","j",10.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,8,8,0,"j","n",10.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,8,14,0,"j","n",9.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,9,1,0,"j","n",7.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,9,7,0,"j","n",7.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,9,10,0,"j","n",8.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,7,9,21,0,"j","n",9.1,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,1,10,3,0,"j","j",6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,1,10,11,0,"j","j",10.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,1,10,20,0,"j","j",11.3,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,11,1,0,"j","j",9.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,11,13,0,"j","j",17.7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,11,18,0,"j","j",18.5,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,2,11,22,0,"j","j",13.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,12,8,0,"j","j",12.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,12,15,0,"j","j",18.8,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,3,12,24,0,"j","j",9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,13,7,0,"j","j",5.0999999999999996,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,13,17,0,"j","j",11.9,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,4,13,21,0,"j","j",7,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,14,10,0,"j","j",11.2,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,14,11,0,"j","j",12.6,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,5,14,19,0,"j","j",13.4,null,null,0,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,9,6,15,8,1,"j","n",8.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,6,15,12,1,"j","n",14.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,6,15,18,1,"j","n",14.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,7,16,5,1,"j","n",9.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,7,16,8,1,"j","n",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,9,7,16,22,1,"j","n",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,9,1,17,5,1,"j","j",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,9,1,17,7,1,"j","j",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,9,1,17,16,1,"j","j",9.4,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,2,18,4,1,"j","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,9,2,18,9,1,"j","j",4.5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,9,2,18,18,1,"j","j",8.6999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,3,19,2,1,"j","j",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,9,3,19,8,1,"j","j",3.3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,9,3,19,11,1,"j","j",8.8000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,9,4,20,1,1,"j","j",5.0999999999999996,null,null,16,null,null,{"$f":"IF(($L6310-$I6310)/(($C$4-$C$16))>=O$21,1*$F6310,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,9,4,20,4,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,9,4,20,15,1,"j","j",10.3,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,4,20,21,1,"j","j",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,9,5,21,5,1,"j","j",5.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,9,5,21,14,1,"j","j",8.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,9,5,21,19,1,"j","j",8.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,5,21,23,1,"j","j",7.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,9,6,22,8,1,"j","n",8.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,6,22,18,1,"j","n",9.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,7,23,1,1,"j","n",7.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,9,7,23,8,1,"j","n",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,9,7,23,18,1,"j","n",13.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,1,24,1,1,"j","j",8.3000000000000007,null,null,16,null,null,{"$f":"IF(($L6406-$I6406)/(($C$4-$C$16))>=O$21,1*$F6406,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,9,1,24,11,1,"j","j",11.5,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,1,24,15,1,"j","j",14.7,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,1,24,20,1,"j","j",11.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,2,25,5,1,"j","j",9.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,2,25,13,1,"j","j",11.2,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,2,25,19,1,"j","j",12.1,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,3,26,6,1,"j","j",10.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,3,26,12,1,"j","j",14.2,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,3,26,23,1,"j","j",8.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,3,26,24,1,"j","j",8.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,4,27,8,1,"j","j",9.3000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,4,27,17,1,"j","j",15.1,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,5,28,1,1,"j","j",10.199999999999999,null,null,16,null,null,{"$f":"IF(($L6502-$I6502)/(($C$4-$C$16))>=O$21,1*$F6502,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,9,5,28,10,1,"j","j",11.6,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,5,28,15,1,"j","j",15.4,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,9,6,29,3,1,"j","n",10.5,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,6,29,5,1,"j","n",10,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,6,29,12,1,"j","n",11.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,9,7,30,2,{"$f":"IF(AND(B6551>$D$13,B6551<$I$13),0,IF(B6551=$D$13,IF(D6551>=$D$12,0,1),IF(B6551=$I$13,IF(D6551<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C6551=7),AND($I$9=1,C6551>5)),\"n\",IF($I$9=2,G6551,\"j\"))","v":"n"},7.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,9,7,30,5,1,"j","n",7.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,9,7,30,12,1,"j","n",9.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,9,7,30,22,1,"j","n",9.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,1,1,2,1,"j","j",12.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,1,1,15,1,"j","j",12.8,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,1,1,24,1,"j","j",11.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,2,2,1,1,"j","j",11.6,null,null,16,null,null,{"$f":"IF(($L6598-$I6598)/(($C$4-$C$16))>=O$21,1*$F6598,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,10,2,2,9,1,"j","j",11.2,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,2,2,22,1,"j","j",9.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,3,3,2,1,"j","j",9.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,3,3,12,1,"j","j",12.7,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,3,3,19,1,"j","j",11.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,4,4,2,1,"j","j",10.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,4,4,12,1,"j","j",11,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,4,4,19,1,"j","j",9.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,4,4,21,1,"j","j",9.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,5,5,9,1,"j","j",5.7,null,null,{"$f":"IF(AND(H6678=\"j\",OR(AND($C$9<=E6678,E6678<$C$10),AND($D$9<=E6678,E6678<$D$10))),$J$5,$C$5)*F6678","v":17},null,null,{"$f":"IF(($L6678-$I6678)/(($C$4-$C$16))>=O$21,1*$F6678,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,10,5,5,14,1,"j","j",9.5,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,5,5,23,1,"j","j",7.8,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,6,6,7,1,"j","n",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,6,6,16,1,"j","n",14.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,6,6,22,1,"j","n",14.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,7,7,1,1,"j","n",14.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,7,7,12,1,"j","n",15.6,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,7,7,18,1,"j","n",17.3,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,10,1,8,2,{"$f":"IF(AND(B6743>$D$13,B6743<$I$13),0,IF(B6743=$D$13,IF(D6743>=$D$12,0,1),IF(B6743=$I$13,IF(D6743<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C6743=7),AND($I$9=1,C6743>5)),\"n\",IF($I$9=2,G6743,\"j\"))","v":"j"},8.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,1,8,11,1,"j","j",13.1,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,1,8,19,1,"j","j",15.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,2,9,4,1,"j","j",13.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,2,9,9,1,"j","j",12.4,null,null,17,null,null,{"$f":"IF(($L6774-$I6774)/(($C$4-$C$16))>=O$21,1*$F6774,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,10,2,9,13,1,"j","j",18.600000000000001,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,10,2,9,23,1,"j","j",14.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,3,10,6,1,"j","j",10.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,3,10,13,1,"j","j",18.5,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,10,3,10,23,1,"j","j",13.4,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,4,11,8,1,"j","j",13,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,4,11,12,1,"j","j",17.5,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,0]
[null,10,5,12,1,1,"j","j",13.2,null,null,16,null,null,{"$f":"IF(($L6838-$I6838)/(($C$4-$C$16))>=O$21,1*$F6838,0)","v":0},0,0,0,0,0,0,0,0,1,1]
[null,10,5,12,2,1,"j","j",12.7,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,5,12,10,1,"j","j",9.9,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,5,12,19,1,"j","j",8.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,6,13,3,1,"j","n",6.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,6,13,9,1,"j","n",6.1,null,null,{"$f":"IF(AND(H6870=\"j\",OR(AND($C$9<=E6870,E6870<$C$10),AND($D$9<=E6870,E6870<$D$10))),$J$5,$C$5)*F6870","v":16},null,null,{"$f":"IF(($L6870-$I6870)/(($C$4-$C$16))>=O$21,1*$F6870,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,10,6,13,20,1,"j","n",8,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,6,13,23,1,"j","n",6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,7,14,13,1,"j","n",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,7,14,20,1,"j","n",8.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,7,14,22,1,"j","n",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,1,15,6,1,"j","j",5.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,1,15,15,1,"j","j",7.3,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,1,15,24,1,"j","j",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,10,2,16,5,1,"j","j",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,10,2,16,17,1,"j","j",8,null,null,17,null,null,{"$f":"IF(($L6950-$I6950)/(($C$4-$C$16))>=O$21,1*$F6950,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,10,2,16,19,1,"j","j",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,10,3,17,2,1,"j","j",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,10,3,17,16,1,"j","j",11.5,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,3,17,19,1,"j","j",6.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,4,18,6,1,"j","j",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,10,4,18,12,1,"j","j",4.5999999999999996,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,10,4,18,20,1,"j","j",7.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,5,19,5,1,"j","j",7.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,5,19,13,1,"j","j",8.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,5,19,14,1,"j","j",8.1999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,6,20,3,1,"j","n",9.1,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,6,20,7,1,"j","n",8.9,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,6,20,17,1,"j","n",10.1,null,null,16,null,null,{"$f":"IF(($L7046-$I7046)/(($C$4-$C$16))>=O$21,1*$F7046,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,10,6,20,24,1,"j","n",8.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,7,21,9,1,"j","n",6.3,null,null,{"$f":"IF(AND(H7062=\"j\",OR(AND($C$9<=E7062,E7062<$C$10),AND($D$9<=E7062,E7062<$D$10))),$J$5,$C$5)*F7062","v":16},null,null,{"$f":"IF(($L7062-$I7062)/(($C$4-$C$16))>=O$21,1*$F7062,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,10,7,21,16,1,"j","n",9.3000000000000007,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,1,22,2,1,"j","j",7.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,1,22,6,1,"j","j",7.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,1,22,11,1,"j","j",8.1,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,1,22,20,1,"j","j",8.6,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,2,23,4,1,"j","j",6.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,2,23,13,1,"j","j",11.3,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,2,23,21,1,"j","j",10.8,null,null,16,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,10,3,24,3,1,"j","j",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,3,24,14,1,"j","j",10.4,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,3,24,17,1,"j","j",10.199999999999999,null,null,17,null,null,{"$f":"IF(($L7142-$I7142)/(($C$4-$C$16))>=O$21,1*$F7142,0)","v":0},0,0,0,0,0,0,0,1,1,1]
[null,10,3,24,23,1,"j","j",9.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,4,25,7,1,"j","j",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,4,25,16,1,"j","j",14.5,null,null,17,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,10,5,26,1,1,"j","j",5.7,null,null,16,null,null,{"$f":"IF(($L7174-$I7174)/(($C$4-$C$16))>=O$21,1*$F7174,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,10,5,26,6,1,"j","j",6.1,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,5,26,18,{"$f":"IF(AND(B7191>$D$13,B7191<$I$13),0,IF(B7191=$D$13,IF(D7191>=$D$12,0,1),IF(B7191=$I$13,IF(D7191<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C7191=7),AND($I$9=1,C7191>5)),\"n\",IF($I$9=2,G7191,\"j\"))","v":"j"},9.6999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,5,26,23,1,"j","j",7.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,6,27,3,1,"j","n",7.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,6,27,13,1,"j","n",7.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,6,27,20,1,"j","n",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,7,28,3,1,"j","n",6.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,7,28,13,1,"j","n",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,10,7,28,17,1,"j","n",5.0999999999999996,null,null,16,null,null,{"$f":"IF(($L7238-$I7238)/(($C$4-$C$16))>=O$21,1*$F7238,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,10,1,29,6,1,"n","j",7.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,1,29,14,1,"n","j",9.6999999999999993,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,1,29,15,1,"n","j",10,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,10,1,29,24,1,"n","j",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,10,2,30,8,1,"n","j",7.3,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,10,2,30,17,1,"n","j",5.7,null,null,17,null,null,{"$f":"IF(($L7286-$I7286)/(($C$4-$C$16))>=O$21,1*$F7286,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,10,2,30,23,1,"n","j",4.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,10,3,31,10,1,"n","j",3.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,10,3,31,13,1,"n","j",5.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,4,1,3,1,"n","j",6.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,4,1,10,1,"n","j",9.3000000000000007,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,4,1,12,1,"n","j",13,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,11,4,1,24,1,"n","j",8.6999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,5,2,5,1,"n","j",6.9,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,5,2,10,1,"n","j",12,null,null,17,null,null,0,0,0,0,0,0,0,0,0,1,1]
[null,11,5,2,22,1,"n","j",8.6999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,6,3,7,1,"n","n",7.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,6,3,15,1,"n","n",15.2,null,null,16,null,null,0,0,0,0,0,0,0,0,0,0,1]
[null,11,6,3,21,1,"n","n",8.1999999999999993,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,6,3,24,1,"n","n",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,7,4,9,1,"n","n",6.1,null,null,16,null,null,{"$f":"IF(($L7398-$I7398)/(($C$4-$C$16))>=O$21,1*$F7398,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,11,7,4,20,1,"n","n",6.3,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,1,5,2,1,"j","j",6.5,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,1,5,10,1,"j","j",5.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,1,5,19,1,"j","j",4.9000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,1,5,24,1,"j","j",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,2,6,4,1,"j","j",5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,2,6,17,1,"j","j",7.3,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,2,6,21,1,"j","j",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,3,7,7,1,"j","j",7.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,3,7,14,1,"j","j",9.6,null,null,17,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,3,7,21,1,"j","j",8.4,null,null,16,null,null,0,0,0,0,0,0,0,0,1,1,1]
[null,11,4,8,7,1,"j","j",6.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,4,8,11,1,"j","j",7.4,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,4,8,16,1,"j","j",7.6,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,5,9,1,1,"j","j",7,null,null,{"$f":"IF(AND(H7510=\"j\",OR(AND($C$9<=E7510,E7510<$C$10),AND($D$9<=E7510,E7510<$D$10))),$J$5,$C$5)*F7510","v":16},null,null,{"$f":"IF(($L7510-$I7510)/(($C$4-$C$16))>=O$21,1*$F7510,0)","v":0},0,0,0,0,0,0,1,1,1,1]
[null,11,5,9,10,1,"j","j",6.7,null,null,17,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,5,9,18,1,"j","j",6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,5,9,24,1,"j","j",6.4,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,6,10,11,1,"j","n",6.2,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,6,10,17,1,"j","n",7.6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,7,11,4,1,"j","n",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,7,11,7,1,"j","n",1.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,7,11,13,1,"j","n",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,7,11,21,1,"j","n",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,1,12,6,1,"j","j",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,1,12,11,1,"j","j",2.2000000000000002,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,1,12,23,1,"j","j",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,2,13,4,1,"j","j",7.7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,2,13,16,1,"j","j",5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,2,13,17,1,"j","j",4.5999999999999996,null,null,17,null,null,{"$f":"IF(($L7622-$I7622)/(($C$4-$C$16))>=O$21,1*$F7622,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,11,3,14,7,1,"j","j",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,3,14,10,{"$f":"IF(AND(B7639>$D$13,B7639<$I$13),0,IF(B7639=$D$13,IF(D7639>=$D$12,0,1),IF(B7639=$I$13,IF(D7639<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C7639=7),AND($I$9=1,C7639>5)),\"n\",IF($I$9=2,G7639,\"j\"))","v":"j"},2.2999999999999998,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,3,14,17,1,"j","j",2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,4,15,3,1,"j","j",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,4,15,7,1,"j","j",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,4,15,20,1,"j","j",-2.1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,5,16,4,1,"j","j",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,5,16,5,1,"j","j",-1.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,5,16,18,1,"j","j",-1.1000000000000001,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,5,16,22,1,"j","j",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,6,17,4,1,"j","n",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,6,17,15,1,"j","n",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,7,18,1,1,"j","n",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,7,18,8,1,"j","n",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,7,18,17,1,"j","n",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,7,18,24,1,"j","n",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,1,19,2,1,"j","j",-1.1000000000000001,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,1,19,14,1,"j","j",-0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,1,19,19,1,"j","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,2,20,4,1,"j","j",4.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,2,20,12,1,"j","j",4.4000000000000004,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,2,20,18,1,"j","j",6,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,11,3,21,5,1,"j","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,3,21,11,1,"j","j",3.1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,3,21,14,1,"j","j",3.9,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,4,22,1,1,"j","j",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,4,22,7,1,"j","j",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,4,22,15,1,"j","j",4.3,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,4,22,24,1,"j","j",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,11,5,23,9,1,"j","j",2.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,5,23,14,1,"j","j",2.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,5,23,18,1,"j","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,6,24,4,1,"j","n",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,6,24,11,1,"j","n",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,6,24,18,1,"j","n",1.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,7,25,4,1,"j","n",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,7,25,11,1,"j","n",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,7,25,21,1,"j","n",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,1,26,1,1,"j","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,1,26,6,1,"j","j",-3.2,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,11,1,26,15,1,"j","j",-1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,1,26,23,1,"j","j",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,2,27,5,1,"j","j",-2.1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,2,27,16,1,"j","j",-0.6,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,3,28,1,1,"j","j",-1.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,3,28,4,1,"j","j",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,3,28,18,1,"j","j",0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,4,29,1,1,"j","j",0.7,null,null,16,null,null,{"$f":"IF(($L7990-$I7990)/(($C$4-$C$16))>=O$21,1*$F7990,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,11,4,29,3,1,"j","j",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,4,29,11,1,"j","j",0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,11,4,29,20,1,"j","j",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,5,30,1,1,"j","j",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,5,30,13,1,"j","j",3.1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,11,5,30,22,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,1,6,1,"j","n",-5.0999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,12,6,1,12,1,"j","n",-7.2,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,12,6,1,15,1,"j","n",-6,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,12,6,1,22,1,"j","n",-7.7,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,12,7,2,8,1,"j","n",-10.7,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,12,7,2,17,1,"j","n",-8.8000000000000007,null,null,16,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,12,1,3,1,1,"j","j",-10.5,null,null,{"$f":"IF(AND(H8086=\"j\",OR(AND($C$9<=E8086,E8086<$C$10),AND($D$9<=E8086,E8086<$D$10))),$J$5,$C$5)*F8086","v":16},null,null,{"$f":"IF(($L8086-$I8086)/(($C$4-$C$16))>=O$21,1*$F8086,0)","v":0},1,1,1,1,1,1,1,1,1,1]
[null,12,1,3,10,1,"j","j",-9.3000000000000007,null,null,17,null,null,0,1,1,1,1,1,1,1,1,1,1]
[null,12,1,3,18,1,"j","j",-6.2,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,12,1,3,19,1,"j","j",-6.1,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,12,2,4,8,1,"j","j",-0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,4,12,1,"j","j",0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,4,22,1,"j","j",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,5,5,1,"j","j",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,5,12,1,"j","j",4.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,3,5,22,1,"j","j",4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,6,5,1,"j","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,6,7,1,"j","j",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,6,19,1,"j","j",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,6,24,1,"j","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,7,9,1,"j","j",0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,5,7,18,1,"j","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,8,2,1,"j","n",7,null,null,16,null,null,0,0,0,0,0,0,0,1,1,1,1]
[null,12,6,8,8,1,"j","n",3.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,8,19,1,"j","n",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,6,8,22,1,"j","n",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,9,4,1,"j","n",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,9,12,1,"j","n",-2.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,9,21,1,"j","n",-5.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,12,1,10,5,1,"j","j",-6.2,null,null,16,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,12,1,10,14,1,"j","j",-2,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,12,1,10,19,1,"j","j",-4.5999999999999996,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,12,2,11,7,1,"j","j",-4.5,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,12,2,11,9,1,"j","j",-5,null,null,17,null,null,0,0,1,1,1,1,1,1,1,1,1]
[null,12,2,11,16,1,"j","j",-2.2999999999999998,null,null,17,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,12,3,12,1,1,"j","j",-1.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,12,8,1,"j","j",-1.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,12,18,1,"j","j",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,12,22,1,"j","j",-0.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,4,13,11,1,"j","j",2.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,13,19,1,"j","j",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,13,20,1,"j","j",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,14,5,1,"j","j",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,14,13,1,"j","j",0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,5,14,19,1,"j","j",-1.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,6,15,6,1,"j","n",-2.2000000000000002,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,6,15,16,1,"j","n",-1.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,6,15,23,1,"j","n",-2.2999999999999998,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,16,6,1,"j","n",-2.2000000000000002,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,16,8,1,"j","n",-2.2999999999999998,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,16,17,1,"j","n",-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,17,5,1,"j","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,17,10,1,"j","j",-1.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,17,19,1,"j","j",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,18,3,1,"j","j",-1.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,18,12,1,"j","j",-1.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,18,20,1,"j","j",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,19,2,{"$f":"IF(AND(B8471>$D$13,B8471<$I$13),0,IF(B8471=$D$13,IF(D8471>=$D$12,0,1),IF(B8471=$I$13,IF(D8471<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C8471=7),AND($I$9=1,C8471>5)),\"n\",IF($I$9=2,G8471,\"j\"))","v":"j"},-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,19,5,1,"j","j",-1.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,19,16,1,"j","j",1.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,3,19,22,1,"j","j",0.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,20,6,1,"j","j",2.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,20,15,1,"j","j",3.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,4,20,23,1,"j","j",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,21,8,1,"j","j",1.2,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,9,1,"j","j",1.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,17,1,"j","j",3.4,null,null,{"$f":"IF(AND(H8534=\"j\",OR(AND($C$9<=E8534,E8534<$C$10),AND($D$9<=E8534,E8534<$D$10))),$J$5,$C$5)*F8534","v":17},null,null,{"$f":"IF(($L8534-$I8534)/(($C$4-$C$16))>=O$21,1*$F8534,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,18,{"$f":"IF(AND(B8535>$D$13,B8535<$I$13),0,IF(B8535=$D$13,IF(D8535>=$D$12,0,1),IF(B8535=$I$13,IF(D8535<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C8535=7),AND($I$9=1,C8535>5)),\"n\",IF($I$9=2,G8535,\"j\"))","v":"j"},2.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,21,19,1,"j","j",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,20,1,"j","j",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,21,1,"j","j",2.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,21,22,1,"j","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,21,23,1,"j","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,5,21,24,1,"j","j",2.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,22,1,1,"j","n",1.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,22,2,1,"j","n",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,22,3,1,"j","n",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,22,4,1,"j","n",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,22,5,1,"j","n",0.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,22,6,1,"j","n",0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,22,7,1,"j","n",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,22,8,1,"j","n",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,22,9,1,"j","n",1.5,null,null,16,null,null,{"$f":"IF(($L8550-$I8550)/(($C$4-$C$16))>=O$21,1*$F8550,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,6,22,10,1,"j","n",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,22,11,1,"j","n",2.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,12,1,"j","n",3.4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,13,1,"j","n",4,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,14,1,"j","n",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,15,1,"j","n",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,16,1,"j","n",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,17,1,"j","n",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,18,1,"j","n",4.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,19,1,"j","n",4.5999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,20,1,"j","n",4.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,21,1,"j","n",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,22,1,"j","n",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,23,1,"j","n",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,6,22,24,1,"j","n",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,1,1,"j","n",3.1,null,null,16,null,null,{"$f":"IF(($L8566-$I8566)/(($C$4-$C$16))>=O$21,1*$F8566,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,2,1,"j","n",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,3,1,"j","n",3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,4,1,"j","n",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,5,1,"j","n",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,6,1,"j","n",2.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,23,7,1,"j","n",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,23,8,1,"j","n",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,23,9,1,"j","n",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,23,10,1,"j","n",2.2000000000000002,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,23,11,1,"j","n",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,23,12,1,"j","n",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,13,1,"j","n",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,14,1,"j","n",3.3,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,15,1,"j","n",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,16,1,"j","n",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,17,1,"j","n",3.1,null,null,16,null,null,{"$f":"IF(($L8582-$I8582)/(($C$4-$C$16))>=O$21,1*$F8582,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,18,1,"j","n",2.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,23,19,1,"j","n",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,23,20,1,"j","n",2.2999999999999998,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,23,21,1,"j","n",3.1,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,22,1,"j","n",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,23,1,"j","n",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,7,23,24,1,"j","n",4.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,1,1,"j","j",4.4000000000000004,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,2,1,"j","j",4.0999999999999996,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,3,1,"j","j",3.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,4,1,"j","j",3.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,5,1,"j","j",3.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,6,1,"j","j",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,7,1,"j","j",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,8,1,"j","j",3.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,24,9,1,"j","j",3.3,null,null,{"$f":"IF(AND(H8598=\"j\",OR(AND($C$9<=E8598,E8598<$C$10),AND($D$9<=E8598,E8598<$D$10))),$J$5,$C$5)*F8598","v":17},null,null,{"$f":"IF(($L8598-$I8598)/(($C$4-$C$16))>=O$21,1*$F8598,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,1,24,10,{"$f":"IF(AND(B8599>$D$13,B8599<$I$13),0,IF(B8599=$D$13,IF(D8599>=$D$12,0,1),IF(B8599=$I$13,IF(D8599<$I$12,0,1),1)))","v":1},"j",{"$f":"IF(OR(AND($I$9=3,C8599=7),AND($I$9=1,C8599>5)),\"n\",IF($I$9=2,G8599,\"j\"))","v":"j"},3.3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,24,11,1,"j","j",3.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,1,24,12,1,"j","j",4,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,13,1,"j","j",4.4000000000000004,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,14,1,"j","j",4.5999999999999996,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,15,1,"j","j",4.5,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,16,1,"j","j",4.2,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,17,1,"j","j",3.8,null,null,17,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,18,1,"j","j",3.5,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,19,1,"j","j",3.2,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,20,1,"j","j",2.9,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,21,1,"j","j",2.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,22,1,"j","j",2.6,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,23,1,"j","j",2.7,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,1,24,24,1,"j","j",2.8,null,null,16,null,null,0,0,0,0,0,0,1,1,1,1,1]
[null,12,2,25,1,1,"n","j",2.8,null,null,16,null,null,{"$f":"IF(($L8614-$I8614)/(($C$4-$C$16))>=O$21,1*$F8614,0)","v":0},0,0,0,0,0,1,1,1,1,1]
[null,12,2,25,2,1,"n","j",2.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,2,25,3,1,"n","j",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,2,25,4,1,"n","j",1.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,2,25,5,1,"n","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,2,25,6,1,"n","j",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,2,25,7,1,"n","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,2,25,8,1,"n","j",0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,9,1,"n","j",0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,10,1,"n","j",0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,11,1,"n","j",0,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,12,1,"n","j",-0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,13,1,"n","j",-0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,14,1,"n","j",-0.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,15,1,"n","j",-0.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,16,1,"n","j",-0.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,17,1,"n","j",-0.5,null,null,17,null,null,{"$f":"IF(($L8630-$I8630)/(($C$4-$C$16))>=O$21,1*$F8630,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,18,1,"n","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,19,1,"n","j",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,20,1,"n","j",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,21,1,"n","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,22,1,"n","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,23,1,"n","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,2,25,24,1,"n","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,1,1,"n","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,2,1,"n","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,3,1,"n","j",-0.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,4,1,"n","j",-0.9,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,5,1,"n","j",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,6,1,"n","j",-1.1000000000000001,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,7,1,"n","j",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,8,1,"n","j",-1.3,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,9,1,"n","j",-1.3,null,null,17,null,null,{"$f":"IF(($L8646-$I8646)/(($C$4-$C$16))>=O$21,1*$F8646,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,10,1,"n","j",-1.1000000000000001,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,11,1,"n","j",-0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,12,1,"n","j",-0.1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,13,1,"n","j",0.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,14,1,"n","j",1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,3,26,15,1,"n","j",1.1000000000000001,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,3,26,16,1,"n","j",1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,3,26,17,1,"n","j",0.6,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,18,1,"n","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,3,26,19,1,"n","j",-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,20,1,"n","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,21,1,"n","j",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,22,1,"n","j",-0.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,23,1,"n","j",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,3,26,24,1,"n","j",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,4,27,1,1,"n","j",-0.1,null,null,{"$f":"IF(AND(H8662=\"j\",OR(AND($C$9<=E8662,E8662<$C$10),AND($D$9<=E8662,E8662<$D$10))),$J$5,$C$5)*F8662","v":16},null,null,{"$f":"IF(($L8662-$I8662)/(($C$4-$C$16))>=O$21,1*$F8662,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,2,{"$f":"IF(AND(B8663>$D$13,B8663<$I$13),0,IF(B8663=$D$13,IF(D8663>=$D$12,0,1),IF(B8663=$I$13,IF(D8663<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C8663=7),AND($I$9=1,C8663>5)),\"n\",IF($I$9=2,G8663,\"j\"))","v":"j"},0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,3,1,"n","j",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,4,1,"n","j",0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,5,1,"n","j",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,6,1,"n","j",0.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,7,1,"n","j",0.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,8,1,"n","j",0.5,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,4,27,9,1,"n","j",0.6,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,4,27,10,1,"n","j",0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,4,27,11,1,"n","j",1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,12,1,"n","j",1.3,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,13,1,"n","j",1.5,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,14,1,"n","j",1.7,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,15,1,"n","j",1.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,16,1,"n","j",1.9,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,17,1,"n","j",1.8,null,null,17,null,null,{"$f":"IF(($L8678-$I8678)/(($C$4-$C$16))>=O$21,1*$F8678,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,18,1,"n","j",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,19,1,"n","j",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,20,1,"n","j",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,21,1,"n","j",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,22,1,"n","j",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,23,1,"n","j",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,4,27,24,1,"n","j",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,1,1,"n","j",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,2,1,"n","j",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,3,1,"n","j",0.9,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,4,1,"n","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,5,1,"n","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,6,1,"n","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,7,1,"n","j",0.8,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,8,1,"n","j",0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,5,28,9,1,"n","j",0.9,null,null,17,null,null,{"$f":"IF(($L8694-$I8694)/(($C$4-$C$16))>=O$21,1*$F8694,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,10,1,"n","j",1,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,11,1,"n","j",1.1000000000000001,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,12,1,"n","j",1.4,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,13,1,"n","j",1.6,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,14,1,"n","j",1.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,15,1,"n","j",1.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,16,1,"n","j",1.8,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,17,1,"n","j",1.6,null,null,17,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,18,1,"n","j",1.5,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,19,1,"n","j",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,20,1,"n","j",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,21,1,"n","j",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,22,1,"n","j",1.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,23,1,"n","j",1.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,5,28,24,1,"n","j",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,1,1,"n","n",1.6,null,null,16,null,null,{"$f":"IF(($L8710-$I8710)/(($C$4-$C$16))>=O$21,1*$F8710,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,2,1,"n","n",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,3,1,"n","n",1.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,4,1,"n","n",1.4,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,5,1,"n","n",1.1000000000000001,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,6,1,"n","n",0.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,7,1,"n","n",0.2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,8,1,"n","n",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,6,29,9,1,"n","n",-0.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,6,29,10,1,"n","n",-0.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,6,29,11,1,"n","n",0.3,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,12,1,"n","n",1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,13,1,"n","n",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,14,1,"n","n",2.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,15,1,"n","n",2,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,16,1,"n","n",1.7,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,17,1,"n","n",1.2,null,null,{"$f":"IF(AND(H8726=\"j\",OR(AND($C$9<=E8726,E8726<$C$10),AND($D$9<=E8726,E8726<$D$10))),$J$5,$C$5)*F8726","v":16},null,null,{"$f":"IF(($L8726-$I8726)/(($C$4-$C$16))>=O$21,1*$F8726,0)","v":0},0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,18,{"$f":"IF(AND(B8727>$D$13,B8727<$I$13),0,IF(B8727=$D$13,IF(D8727>=$D$12,0,1),IF(B8727=$I$13,IF(D8727<$I$12,0,1),1)))","v":1},"n",{"$f":"IF(OR(AND($I$9=3,C8727=7),AND($I$9=1,C8727>5)),\"n\",IF($I$9=2,G8727,\"j\"))","v":"n"},0.6,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,19,1,"n","n",0,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,6,29,20,1,"n","n",-0.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,6,29,21,1,"n","n",-1.1000000000000001,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,6,29,22,1,"n","n",-1.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,6,29,23,1,"n","n",-1.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,6,29,24,1,"n","n",-1.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,1,1,"n","n",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,2,1,"n","n",-1.2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,3,1,"n","n",-1.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,4,1,"n","n",-1.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,5,1,"n","n",-2.1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,6,1,"n","n",-2.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,7,1,"n","n",-3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,12,7,30,8,1,"n","n",-3.3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,12,7,30,9,1,"n","n",-3.3,null,null,16,null,null,{"$f":"IF(($L8742-$I8742)/(($C$4-$C$16))>=O$21,1*$F8742,0)","v":0},0,0,1,1,1,1,1,1,1,1]
[null,12,7,30,10,1,"n","n",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,12,7,30,11,1,"n","n",-2.1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,12,1,"n","n",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,13,1,"n","n",-0.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,14,1,"n","n",-0.1,null,null,16,null,null,0,0,0,0,0,1,1,1,1,1,1]
[null,12,7,30,15,1,"n","n",-0.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,16,1,"n","n",-1.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,17,1,"n","n",-2.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,18,1,"n","n",-3,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,12,7,30,19,1,"n","n",-2.9,null,null,16,null,null,0,0,0,1,1,1,1,1,1,1,1]
[null,12,7,30,20,1,"n","n",-2.4,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,21,1,"n","n",-1.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,22,1,"n","n",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,23,1,"n","n",-1.1000000000000001,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,7,30,24,1,"n","n",-1.7,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,1,1,"n","j",-2.5,null,null,16,null,null,{"$f":"IF(($L8758-$I8758)/(($C$4-$C$16))>=O$21,1*$F8758,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,2,1,"n","j",-2.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,3,1,"n","j",-2.2999999999999998,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,4,1,"n","j",-2,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,5,1,"n","j",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,6,1,"n","j",-1.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,7,1,"n","j",-1.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,8,1,"n","j",-1.4,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,9,1,"n","j",-1.2,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,10,1,"n","j",-1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,11,1,"n","j",-1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,12,1,"n","j",-1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,13,1,"n","j",-1,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,14,1,"n","j",-0.9,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,15,1,"n","j",-0.8,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,16,1,"n","j",-0.7,null,null,17,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,17,1,"n","j",-0.8,null,null,17,null,null,{"$f":"IF(($L8774-$I8774)/(($C$4-$C$16))>=O$21,1*$F8774,0)","v":0},0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,18,1,"n","j",-1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,19,1,"n","j",-1.3,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,20,1,"n","j",-1.5,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,21,1,"n","j",-1.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,22,1,"n","j",-1.6,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,23,1,"n","j",-1.8,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,12,1,31,24,1,"n","j",-2.1,null,null,16,null,null,0,0,0,0,1,1,1,1,1,1,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(O22:O8781)","v":10},106,238,578,1717,2834,3799,4685,5259,5522,5707]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Ces données sont rapatriées dans le cadre 4 de l'onglet \"Rendement saisonnier\""]

{"sheet":"Données","index":5,"n_rows":103,"n_cols":15,"rows_kept":103,"cut":false,"hidden":true,"merged":[]}
["Combustible utilisé par la chaufferie",null,null,null,null,null,"PCS MJ/m³ ou litre","PCI MJ/m³ ou litre","kWh pcs/m³ ou litre","kWh pci/m³ ou litre","PCI/PCS","Conversion"]
["Gaz pauvre L - G25 (Bruxelles et brabant wallon)",null,null,null,null,null,36.9,33.299999999999997,{"$f":"G2/3.6","v":10.25},9.2499999999999982,{"$f":"J2/I2","v":0.9024390243902437},0.90200000000000002]
["Gaz riche H - G20 (Wallonie, hors brabant wallon)",null,null,null,null,null,42.9,38.700000000000003,11.916666666666666,10.75,{"$f":"J3/I3","v":0.90209790209790219},0.90200000000000002,null,"Gaz naturel"]
["Fuel",null,null,null,null,null,38.1,35.799999999999997,10.583333333333334,9.9444444444444429,{"$f":"J4/I4","v":0.93963254593175838},9.94,null,"Mazout"]
["Cellule :",1,{"$f":"INDEX(A2:A4,B5,1)","v":"Gaz pauvre L - G25 (Bruxelles et brabant wallon)"},null,null,null,{"$f":"INDEX(G2:G4,$B$5,1)","v":36.9},33.299999999999997,10.25,9.2499999999999982,0.9024390243902437,{"$f":"INDEX(L2:L4,$B$5,1)","v":0.90200000000000002}]
[]
["Unité combustible"]
[{"$f":"IF(B5=3,\"litres de mazout\",\"- (ne pas sélectionner ce choix)\")","v":"- (ne pas sélectionner ce choix)"}]
[{"$f":"IF(B5=3,\"-\",\"- (ne pas sélectionner ce choix)\")","v":"- (ne pas sélectionner ce choix)"}]
[{"$f":"IF(B5=3,\"-\",\"kWh de gaz PCS\")","v":"kWh de gaz PCS"}]
["Cellule :",3,{"$f":"INDEX(A8:A10,B11,1)","v":"kWh de gaz PCS"}]
[]
["Profil de fonctionnement hebdomadaire"]
["5 jours sur 7 (jours ouvrables)"]
["5 jours sur 7 (calendrier scolaire)"]
["6 jours sur 7 (y compris le samedi)"]
["7 jours sur 7"]
[]
["Type de chaudière"]
[{"$f":"IF(B5=3,\"Chaudière fuel\",\"-\")","v":"-"}]
[{"$f":"IF(B5=3,\"-\",\"Chaudière gaz à brûleur pulsé\")","v":"Chaudière gaz à brûleur pulsé"}]
[{"$f":"IF(B5=3,\"-\",\"Chaudière gaz atmosphérique\")","v":"Chaudière gaz atmosphérique"}]
[]
["Type de brûleur"]
["Brûleur 1 allure ou brûleur avec petite allure de démarrage"]
["Brûleur 2 allures 60 / 100% (régulé en cascade)"]
["Cellule :",{"$f":"'Calcul du rendement'!P82","v":1}]
[]
["Régulation des chaudières"]
["Fonctionnement en parallèle"]
["Régulation en cascade mais maintien de l'irrigation de toutes les chaudières"]
["Régulation en cascade avec arrêt de l'irrigation des chaudières inutilisées"]
["Cellule :",{"$f":"'Calcul du rendement'!P81","v":3}]
[]
["Etat de l'isolation"]
["Correcte"]
["Déteriorée ou absente"]
[]
["Clapet d'air brûleur"]
["Ouvert"]
["Fermé"]
[]
["Rendement utile par défaut des chaudières atmosphériques"]
["Année limite","Rendement de combustion"]
[2050,90]
[1985,87]
[1975,85]
[]
["Gammes de température retenues pour la définition du rendement d'une chaudière à condensation"]
["T° retour chaudière"]
["Inférieure à 45°C"]
["Comprise entre 45 et 55°C"]
["Supérieure à 55°C"]
[]
["Faisceau de présomptions concernant la température de retour des chaudières à condensation"]
["BP","RCTG","RCSTG"]
[1,1,1,{"$f":"A57&B57&C57","v":"111"},"Inférieure à 45°C",null,null,"BP","= By Pass (bouclage collecteur ou bouteille casse-pression ou vannes de régulation diviseuses)",null,null,null,null,null,2]
[1,1,2,{"$f":"A58&B58&C58","v":"112"},"Inférieure à 45°C",null,null,"si 1","Absence = bon"]
[1,1,3,"113","Inférieure à 45°C",null,null,"si 2","Présence = mauvais"]
[1,2,1,"121","Inférieure à 45°C",null,null,"RCTG","= Régulation chaudière en température glissante",null,null,null,null,null,2]
[1,2,2,"122","Supérieure à 55°C",null,null,"si 1","Présente et bien réglée (max 5°C au-dessus du circuit le plus demandeur)"]
[1,2,3,"123","Comprise entre 45 et 55°C",null,null,"si 2","Absente ou mal réglée (plus de 15°C au-dessus du circuit le plus demandeur)"]
[1,3,1,"131","Inférieure à 45°C",null,null,"si 3","Partiellement bien réglée (max 15°C au-dessus du circuit le plus demandeur)"]
[1,3,2,"132","Supérieure à 55°C",null,null,"RCSTG","= Régulation circuits secondaires en température glissante",null,null,null,null,null,2]
[1,3,3,"133","Comprise entre 45 et 55°C",null,null,"si 1","Présente et bien réglée"]
[2,1,1,"211","Inférieure à 45°C",null,null,"si 2","Absente ou mal réglée"]
[2,1,2,"212","Comprise entre 45 et 55°C",null,null,"si 3","Partiellement bon (présence de consommateurs à haute température)"]
[2,1,3,"213","Comprise entre 45 et 55°C"]
[2,2,1,"221","Supérieure à 55°C",null,null,"Cellule BP",1]
[2,2,2,"222","Supérieure à 55°C",null,null,"Cellule RCTG",1]
[2,2,3,"223","Supérieure à 55°C",null,null,"Cellule RCSTG",2]
[2,3,1,"231","Comprise entre 45 et 55°C",null,null,"Combinaison",{"$f":"I69&I70&I71","v":"112"}]
[2,3,2,"232","Supérieure à 55°C"]
[2,3,3,"233","Comprise entre 45 et 55°C"]
[]
["Données pertes à l'arrêt en fonction de l'âge de la chaudière"]
[null,null,null,"Pertes à l'arrêt (75/60°C) en %"]
["Puissance en kW",">01","81-00","76-80","71-75","66-70","<65"]
[90,4.1000000000000003E-3,5.4999999999999997E-3,1.2E-2,1.6500000000000001E-2,2.1999999999999999E-2,2.7E-2]
[100,3.7000000000000002E-3,5.0000000000000001E-3,1.15E-2,1.6E-2,2.1000000000000001E-2,2.5999999999999999E-2]
[150,2.8E-3,4.0000000000000001E-3,9.4999999999999998E-3,1.35E-2,1.7999999999999999E-2,2.2499999999999999E-2]
[300,1.4E-3,3.0000000000000001E-3,7.4999999999999997E-3,1.0500000000000001E-2,1.4999999999999999E-2,1.7500000000000002E-2]
[500,1.2999999999999999E-3,2.5000000000000001E-3,6.0000000000000001E-3,8.5000000000000006E-3,1.2500000000000001E-2,1.4500000000000001E-2]
[1000,1.2999999999999999E-3,2.5000000000000001E-3,4.4999999999999997E-3,7.0000000000000001E-3,0.01,1.15E-2]
[2000,1.1999999999999999E-3,2E-3,4.0000000000000001E-3,5.4999999999999997E-3,8.0000000000000002E-3,0.01]
[5000,1.1000000000000001E-3,1.5E-3,3.5000000000000001E-3,5.0000000000000001E-3,7.0000000000000001E-3,8.9999999999999993E-3]
["Année limite",2050,2000,1980,1975,1970,1965]
["Paramètres",1.38E-2,1.9E-2,4.8599999999999997E-2,6.5500000000000003E-2,8.0699999999999994E-2,9.5299999999999996E-2]
["Paramètres",-0.32779999999999998,-0.30199999999999999,-0.32500000000000001,-0.3165,-0.2964,-0.29160000000000003]
[]
[null,"Chaudière 1","Chaudière 2","Chaudière 3","Chaudière 4"]
[null,{"$f":"INDEX($B$88:$G$89,1,MATCH('Calcul du rendement'!G97,$B$87:$G$87,-1))","v":4.8599999999999997E-2},{"$f":"INDEX($B$88:$G$89,1,MATCH('Calcul du rendement'!H97,$B$87:$G$87,-1))","v":4.8599999999999997E-2},{"$f":"INDEX($B$88:$G$89,1,MATCH('Calcul du rendement'!I97,$B$87:$G$87,-1))","v":9.5299999999999996E-2},{"$f":"INDEX($B$88:$G$89,1,MATCH('Calcul du rendement'!J97,$B$87:$G$87,-1))","v":9.5299999999999996E-2}]
[null,{"$f":"INDEX($B$88:$G$89,2,MATCH('Calcul du rendement'!G97,$B$87:$G$87,-1))","v":-0.32500000000000001},{"$f":"INDEX($B$88:$G$89,2,MATCH('Calcul du rendement'!H97,$B$87:$G$87,-1))","v":-0.32500000000000001},{"$f":"INDEX($B$88:$G$89,2,MATCH('Calcul du rendement'!I97,$B$87:$G$87,-1))","v":-0.29160000000000003},{"$f":"INDEX($B$88:$G$89,2,MATCH('Calcul du rendement'!J97,$B$87:$G$87,-1))","v":-0.29160000000000003}]
[]
["Définition du facteur correctif de la température des pertes à l'arrêt"]
[null,"Température moyenne des chaudières estimée","Facteur de correction du coefficient de perte à l'arrêt"]
["Sur aquatast (à 75°C)","70°C",1]
["Température glissante avec limite basse (à 60°C)","56°C",0.75]
["Température glissante sans limite basse","42°C",0.51]
[]
["Présence chaudière à condensation"]
["Oui"]
["Non"]